## Hydrological Staitons (hidden)
S.no. | Station Name | Station Index | Total Area, km2 | Area below 3000 masl | 3000 masl < Area < 5000 masl | Area above 5000 masl | Area below 5000 masl
1 | Isuwa at Intake | - | 160.79 | 10.02% | 61.68% | 28.3% | 115.28
2 | Powerhouse river-1 | - | 27542.5589 | 2.545% | 58.45% | 39% | 16800.31
3 | Uwa Gaon | 600.1 | 27090.7629 | 1.618% | 58.9% | 39.48% | 16396.2
4 | Sabhaya | 602 | 391.36 | 92.28% | 7.717% | 0% | 391.36
5 | Hinwa | 602.5 | 148.14 | 96.03% | 3.969% | 0% | 148.14
6 | Turkeghat | 604.5 | 28601.8938 | 5.13% | 57.28% | 37.59% | 17849.7

## HYDEST
HYDROLOGICAL CALCULATION
Job | Due Deligence Study of Isuwa Khola HPP
Subject | HYDEST, 1991
Location | ISUWA
Catchment Area | 217.8918 | km2 |  | Monsoon Wetness index |  | 2500
Area Below 5000m | 209.73 | km2 |  | Area Below 3000m |  | 70.31 | km2
Extreme Hydrology
Flood Flow, Q m3/s |  |  | Low Flows
Return Period | Instantaneous | Daily | Return Period | Day | Low flows, Q m3/s
2 | 79.619 | 47.519 | 2 | 1 | 1.5612
5 | 134.0279 | 72.4554 |  | 7 | 1.6464
10 | 175.9495 | 90.3247 |  | 30 | 1.9306
20 | 220.2404 | 108.3399 |  | Monthly | 2.0694
50 | 283.6369 | 132.9778 | 10 | 1 | 0.96484
100 | 335.6042 | 152.3917 |  | 7 | 1.0855
200 | 391.726 | 172.7255 |  | 30 | 1.3672
500 | 472.178 | 200.9399 |  | Monthly | 1.497
1000 | 538.3357 | 223.4567 | 20 | 1 | 0.81722
5000 | 711.1026 | 279.9658 |  | 7 | 0.96392
10000 | 794.3561 | 306.233 |  | 30 | 1.2501
|  |  |  | Monthly | 1.3735
Long term Hydrology
Mean Monthly Flows
Month | Flow, Q m3/s | [6 empty] | C | A1 | A2 | A3
January | 2.6614 | [6 empty] | 0.01423 | 0 | 0.9777 | 0
February | 2.2665 | [6 empty] | 0.01219 | 0 | 0.9766 | 0
March | 2.047 | [6 empty] | 0.009988 | 0 | 0.9948 | 0
April | 2.1207 | [6 empty] | 0.007974 | 0 | 1.0435 | 0
May | 2.8736 | [6 empty] | 0.008434 | 0 | 1.0898 | 0
June | 11.4596 | [6 empty] | 0.006943 | 0.9968 | 0 | 0.261
July | 33.8522 | [6 empty] | 0.02123 | 0 | 1.0093 | 0.2523
August | 40.8873 | [6 empty] | 0.02548 | 0 | 0.9963 | 0.262
September | 31.7362 | [6 empty] | 0.01677 | 0 | 0.9894 | 0.2878
October | 13.6738 | [6 empty] | 0.009724 | 0 | 0.988 | 0.2508
November | 6.6067 | [6 empty] | 0.00176 | 0.9605 | 0 | 0.391
December | 4.2375 | [6 empty] | 0.001485 | 0.9536 | 0 | 0.3607
Mean Monthly Flow | 12.8686
Maximum flow occurred | 40.8873
Minimum flow | 2.047
Flow Duration Curve
Probability of Excedence (%) |  | Discharge
0 |  | 83.0368
5 |  | 46.6315
20 |  | 27.2998
40 |  | 7.3547
50 |  | 5.4769
60 |  | 3.599
65 |  | 3.2029
80 |  | 2.0146
95 |  | 1.342
100 |  | 1.1751
Note on K28: Constant Coefficient
Note on L28: Power, Area of Basin
Note on M28: Power, Area of Basin belo 5000m
Note on N28: Power of Monsoon Wetness Index
Note on C29: Bishnu: Though I calculated this to observe the difference with the FDC from empirical relation, we should stick to the built-in version.

## Modified HYDEST
HYDROLOGICAL CALCULATION
Job | Due Deligence Study of Isuwa Khola HPP
Subject | Modified HYDEST
Location | ISUWA |  | Average altitude | 3492.97 | m
Catchment Area | 217.8918 | km2 | Annual Wetness index | 2500 | mm
Area Below 5000m | 209.73 | km2 | Area Below 3000m | 70.31 | km2
Extreme Hydrology
Flood flows |  |  |  |  | Low Flows |  |  | Flood flows |  |  | Low Flows
Return Period, T yrs |  | Flood flows, Q m3/s |  |  | Return Period | Day | Low flows, Q m3/s | Standard Normal Variate, s |  |  | Cd,T | Fd,T
2 |  | 88.7708 |  |  | 2 | 1 | 1.9452 | 0 |  |  | 0.2144 | 0.0815
5 |  | 158.7744 |  |  |  | 7 | 2.0685 | 0.842 |  |  | 0.2362 | 0.083
10 |  | 215.1462 |  |  |  | 30 | 2.3697 | 1.282 |  |  | 0.3026 | 0.0854
20 |  | 276.4363 |  |  |  | Monthly | 2.5127 | 1.645 |  |  | 0.3397 | 0.086
50 |  | 366.6499 |  |  | 10 | 1 | 1.3033 | 2.054 |  |  | 0.0859 | 0.0729
100 |  | 442.4077 |  |  |  | 7 | 1.3812 | 2.326 |  |  | 0.092 | 0.0748
200 |  | 525.7703 |  |  |  | 30 | 1.6642 | 2.576 |  |  | 0.1807 | 0.0766
500 |  | 647.6851 |  |  |  | Monthly | 1.7931 | 2.878 |  |  | 0.2138 | 0.0777
1000 |  | 749.7929 |  |  | 20 | 1 | 1.1835 | 3.09 |  |  | 0.0698 | 0.0703
5000 |  | 1023.042 |  |  |  | 7 | 1.249 | 3.54 |  |  | 0.0662 | 0.0726
10000 |  | 1157.6424 |  |  |  | 30 | 1.5264 | 3.719 |  |  | 0.1609 | 0.0742
[6 empty] | Monthly | 1.6549 |  |  |  | 0.1945 | 0.0754
Long term Hydrology
Mean Monthly Flows
Month | Flow, Q m3/s
January | 4.7601 | [6 empty] | Const | Elevation | Annual Precipitation | Area below 3000 | Area below 5000
February | 4.1153 | [6 empty] | a | b | c | d | e
March | 2.8964 | [6 empty] | -16.7 | 1.36 | 0.47 | 0.82 | 0
April | 2.8464 | [6 empty] | -17.2 | 1.42 | 0.456 | 0.814 | 0
May | 3.8796 | [6 empty] | 0.384 | 0 | 0 | 0 | 0.091
June | 18.0111 | [6 empty] | 0.181 | 0 | 0 | 0 | 0.104
July | 39.5572 | [6 empty] | 0.0001 | 0 | 0 | 0 | 0.136
August | 53.9142 | [6 empty] | -19.5 | 1.61 | 0.709 | 0.872 | 0
September | 34.7715 | [6 empty] | -16.3 | 1.26 | 0.759 | 0.884 | 0
October | 17.5348 | [6 empty] | -14.7 | 1.24 | 0.622 | 0.871 | 0
November | 8.6446 | [6 empty] | -13.7 | 1.09 | 0.594 | 0.872 | 0
December | 5.9271 | [6 empty] | -15.3 | 1.21 | 0.6 | 0.846 | 0
Mean Monthly Flows | 16.4048 | [6 empty] | -16.7 | 1.36 | 0.543 | 0.826 | 0
Maximum flow occurred | 53.9142 | [6 empty] | -17 | 1.39 | 0.504 | 0.822 | 0
Minimum flow | 2.8464
Ratio | 18.9411
Flow Duration curve | [7 empty] | Const | Elevation | Annual Precipitation | Area below 3000 | Area below 5000
Probability percentage,% |  | Flow, Q m3/s | [5 empty] | a | b | c | d | e
0 |  | 176.0084 | [5 empty] | -12.8 | 0.366 | 0 | 0.529 | 0
5 |  | 49.6933 | [5 empty] | -13.6 | 1.108 | 0.607 | 0.874 | 0
20 |  | 31.3355 | [5 empty] | -17 | 1.359 | 0.716 | 0.883 | 0
40 |  | 11.7535 | [5 empty] | -19 | 1.554 | 0.656 | 0.859 | 0
50 |  | 8.8283
60 |  | 5.9031 | [5 empty] | -18.3 | 1.535 | 0.513 | 0.832 | 0
65 |  | 5.5304
80 |  | 4.4125 | [5 empty] | -19.4 | 1.589 | 0.559 | 0.834 | 0
95 |  | 3.288 | [5 empty] | -21.2 | 1.732 | 0.598 | 0.842 | 0
100 |  | 1.7825 | [5 empty] | -2.18 | 0 | 0.048 | 0 | 0.077

## station_details
S.no. | Station Name | Station Index | Total Area, km2 | Area below 3000 masl | 3000 masl < Area < 5000 masl | Area above 5000 masl | Area below 5000 masl
1 | Isuwa at Intake | - | 160.79 | 10.02% | 61.68% | 28.3% | 115.28
2 | Powerhouse river-1 | - | 27542.5589 | 2.545% | 58.45% | 39% | 16800.31
3 | Powerhouse river-2 | - | 217.8918 | 32.27% | 63.98% | 3.75% | 209.73
4 | Uwa Gaon | 600.1 | 27090.7629 | 1.618% | 58.9% | 39.48% | 16396.2
5 | Sabhaya | 602 | 391.36 | 92.28% | 7.717% | 0% | 391.36
6 | Hinwa | 602.5 | 148.14 | 96.03% | 3.969% | 0% | 148.14
7 | Turkeghat | 604.5 | 28601.8938 | 5.13% | 57.28% | 37.59% | 17849.7

## Modified HYDEST_PH (hidden)
Hydro Consult Pvt.Ltd
HYDROLOGICAL CALCULATION
Job | Middle Modi Hydroelectric Project |  |  | Job No
Subject | Hydrological estimation |  |  | Calculated | SP Bhusal
Date | 2022-02-22 |  |  | Checked
Location | MM HEP |  | Average altitude | 3728 | m
Catchment Area | 503 | km2 | Annual Wetness index | 2800 | mm
Area Below 5000m | 384 | km2 | Area Below 3000m | 213 | km2
Extreme Hydrology
Flood flows |  |  |  |  | Low Flows |  |  | Flood flows |  |  | Low Flows
Return Period, T yrs |  | Flood flows, Q m3/s |  |  | Return Period | Day | Low flows, Q m3/s | Standard Normal Variate, s |  |  | Cd,T | Fd,T
2 |  | 230.2724 |  |  | 2 | 1 | 3.2814 | 0 |  |  | 0.2144 | 0.0815
5 |  | 389.3653 |  |  |  | 7 | 3.4695 | 0.842 |  |  | 0.2362 | 0.083
10 |  | 512.3448 |  |  |  | 30 | 3.9049 | 1.282 |  |  | 0.3026 | 0.0854
20 |  | 642.5495 |  |  |  | Monthly | 4.1004 | 1.645 |  |  | 0.3397 | 0.086
50 |  | 829.3029 |  |  | 10 | 1 | 2.2935 | 2.054 |  |  | 0.0859 | 0.0729
100 |  | 982.6609 |  |  |  | 7 | 2.4267 | 2.326 |  |  | 0.092 | 0.0748
200 |  | 1148.5075 |  |  |  | 30 | 2.8283 | 2.576 |  |  | 0.1807 | 0.0766
500 |  | 1386.6023 |  |  |  | Monthly | 3.0151 | 2.878 |  |  | 0.2138 | 0.0777
1000 |  | 1582.6582 |  |  | 20 | 1 | 2.0949 | 3.09 |  |  | 0.0698 | 0.0703
5000 |  | 2095.5667 |  |  |  | 7 | 2.2167 | 3.54 |  |  | 0.0662 | 0.0726
10000 |  | 2343.1295 |  |  |  | 30 | 2.608 | 3.719 |  |  | 0.1609 | 0.0742
[6 empty] | Monthly | 2.7957 |  |  |  | 0.1945 | 0.0754
Long term Hydrology
Mean Monthly Flows
Month | Flow, Q m3/s
January | 13.6121 | [6 empty] | Const | Elevation | Annual Precipitation | Area below 3000 | Area below 5000
February | 11.7175 | [6 empty] | a | b | c | d | e
March | 4.6969 | [6 empty] | -16.7 | 1.36 | 0.47 | 0.82 | 0
April | 4.9239 | [6 empty] | -17.2 | 1.42 | 0.456 | 0.814 | 0
May | 7.103 | [6 empty] | 0.384 | 0 | 0 | 0 | 0.091
June | 56.9791 | [6 empty] | 0.181 | 0 | 0 | 0 | 0.104
July | 124.6637 | [6 empty] | 0.0001 | 0 | 0 | 0 | 0.136
August | 164.6843 | [6 empty] | -19.5 | 1.61 | 0.709 | 0.872 | 0
September | 104.9623 | [6 empty] | -16.3 | 1.26 | 0.759 | 0.884 | 0
October | 51.8662 | [6 empty] | -14.7 | 1.24 | 0.622 | 0.871 | 0
November | 25.0921 | [6 empty] | -13.7 | 1.09 | 0.594 | 0.872 | 0
December | 17.086 | [6 empty] | -15.3 | 1.21 | 0.6 | 0.846 | 0
Mean Monthly Flows | 48.9489 | [6 empty] | -16.7 | 1.36 | 0.543 | 0.826 | 0
Maximum flow occurred | 164.6843 | [6 empty] | -17 | 1.39 | 0.504 | 0.822 | 0
Minimum flow | 4.6969
Ratio | 35.0625
Average =
Flow Duration curve | [7 empty] | Const | Elevation | Annual Precipitation | Area below 3000 | Area below 5000
Probability percentage,% |  | Flow, Q m3/s | [5 empty] | a | b | c | d | e
0 |  | 298.1662 | [5 empty] | -12.8 | 0.366 | 0 | 0.529 | 0
5 |  | 150.7367 | [5 empty] | -13.6 | 1.108 | 0.607 | 0.874 | 0
20 |  | 98.7993 | [5 empty] | -17 | 1.359 | 0.716 | 0.883 | 0
40 |  | 36.2988 | [5 empty] | -19 | 1.554 | 0.656 | 0.859 | 0
50 |  | 26.843
60 |  | 17.3872 | [5 empty] | -18.3 | 1.535 | 0.513 | 0.832 | 0
65 |  | 16.3254
80 |  | 13.1399 | [5 empty] | -19.4 | 1.589 | 0.559 | 0.834 | 0
95 |  | 10.015 | [5 empty] | -21.2 | 1.732 | 0.598 | 0.842 | 0
100 |  | 3.4924 | [5 empty] | -2.18 | 0 | 0.048 | 0 | 0.077

## COMPARISION (hidden)
HYDROLOGICAL CALCULATION
Job | Kali Gandaki Tinau Diversion Multi Purpose Project
Subject | Comparision of new and old WECS
Flood flows
Return Period, T yrs |  | Flood flows, Q m3/s
|  | DHM 2004 (Modified Hydest) |  | Hydest
2 |  | 88.7708 |  | 79.619
5 |  | 158.7744 |  | 134.0279
10 |  | 215.1462 |  | 175.9495
20 |  | 276.4363 |  | 220.2404
50 |  | 366.6499 |  | 283.6369
100 |  | 442.4077 |  | 335.6042
200 |  | 525.7703 |  | 391.726
500 |  | 647.6851 |  | 472.178
1000 |  | 749.7929 |  | 538.3357
5000 |  | 1023.042 |  | 711.1026
Low Flows
Return Period, T yrs |  | Day | Low flows, Q m3/s
|  |  | DHM 2004 (modified Hydest) |  | Hydest
2 |  | 1 | 1.9452 |  | 1.5612
|  | 7 | 2.0685 |  | 1.6464
|  | 30 | 2.3697 |  | 1.9306
|  | Monthly | 2.5127 |  | 2.0694
10 |  | 1 | 1.3033 |  | 0.96484
|  | 7 | 1.3812 |  | 1.0855
|  | 30 | 1.6642 |  | 1.3672
|  | Monthly | 1.7931 |  | 1.497
20 |  | 1 | 1.1835 |  | 0.81722
|  | 7 | 1.249 |  | 0.96392
|  | 30 | 1.5264 |  | 1.2501
|  | Monthly | 1.6549 |  | 1.3735
Mean Monthly Flows
Mean monthly flows, Q m3/s
Month |  | DHM 2004(Modifed Hydest) | Hydest | MHSP
January |  | 4.7601 | 2.6614 | 2.0393
February |  | 4.1153 | 2.2665 | 2.4854
March |  | 2.8964 | 2.047 | 2.8315
April |  | 2.8464 | 2.1207 | 8.7399
May |  | 3.8796 | 2.8736 | 25.4136
June |  | 18.0111 | 11.4596 | 30.4583
July |  | 39.5572 | 33.8522 | 23.7751
August |  | 53.9142 | 40.8873 | 11.2129
September |  | 34.7715 | 31.7362 | 5.4149
October |  | 17.5348 | 13.6738 | 3.5043
November |  | 8.6446 | 6.6067 | 10.0672
December |  | 5.9271 | 4.2375 | 0
Annual Average |  | 16.4048 | 12.8686 | 10.4952
Flow Duration curve
Probability percentage,% |  | Flow, Q m3/s
|  | DHM 2004 |  | Hydest
0 |  | 176.0084 |  | 83.0368
5 |  | 49.6933 |  | 46.6315
20 |  | 31.3355 |  | 27.2998
40 |  | 11.7535 |  | 7.3547
50 |  | 8.8283 |  | 5.4769
60 |  | 5.9031 |  | 3.599
65 |  | 5.5304 |  | 3.2029
80 |  | 4.4125 |  | 2.0146
95 |  | 3.288 |  | 1.342
100 |  | 1.7825 |  | 1.1751