## efficiency from chart (hidden)
% of Q | Efficiency from available energy curve
100 | 90.5%
90 | 90.5%
80 | 90.5%
70 | 90.5%
60 | 90.5%
50 | 90.5%
Overrating | 90.5%
Design discharge |  | 12.5 | m3/s
No of unit |  | 3
| Per unit discharge | 4.1667
Month | Power Generating Discharge, m³/s | Unit 1 | Unit 2 | Unit 3 | Efficiency | Remarks
Baishakh | 5.654 | 135.7% | 67.85% | 45.23% | 91% | 2 | 90%
Jestha | 11.364 | 272.7% | 136.4% | 90.91% | 91% | 3 | 91%
Ashadh | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Shrawan | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Bhadra | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Ashwin | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Kartik | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Mangshir | 6.674 | 160.2% | 80.09% | 53.39% | 91% | 3 | 89%
Paush | 5.124 | 123% | 61.49% | 40.99% | 91% | 2 | 89%
Magh | 4.104 | 98.5% | 49.25% | 32.83% | 91% | 2 | 90%
Fagun | 3.924 | 94.18% | 47.09% | 31.39% | 91% | 1 | 89%
Chaitra | 3.974 | 95.38% | 47.69% | 31.79% | 91% | 1 | 90%
Note on G16: Jeevika Khadka: efficiency at rated discharge is 91

## Headloss Estimation
JOB TITLE : | Myagdi Khola hydropower Project (65 MW)
JOB NO. : | [22 empty] | Values in these cells are input parameters
SUBJECT : | HEADLOSS ESTIMATION
STRUCTURE : | HEADWORKS TO TAILRACE
Calculated by: | PrM
SN | Description | Governing Equations/ Remarks | Symbol | Unit | Design Parameters | Baisakh | Jestha | Ashad | Srawan | Bhadra | Asoj | Kartik | Mangsir | Poush | Magh | Falgun | Chaitra | Total Energy Level | Water Level
| Turbine Discharge | [40% exceedance flow ] | Q40 | m³/s | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974
| Orifice Discharge |  | Qo | m³/s | 15 | 6.7848 | 13.6368 | 15 | 15 | 15 | 15 | 15 | 8.0088 | 6.1488 | 4.9248 | 4.7088 | 4.7688 | [6 empty] | 15.625
| Settling Basin Discharge |  | Qs | m³/s | 13.75 | 6.2194 | 12.5004 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 7.3414 | 5.6364 | 4.5144 | 4.3164 | 4.3714
| Weir Crest Elevation |  |  | masl | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482
| Bar thickness |  |  | mm | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| No of bars in each rack |  |  | mm | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
| Gross width of rack |  |  | m | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
| Gross ara of racks |  |  | m2 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387 | 9.9387
| Net area of openings |  |  |  | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518 | 17.6518
| Approach Velocity |  | Va | m/s | 0.84977 | 0.38437 | 0.77254 | 0.84977 | 0.84977 | 0.84977 | 0.84977 | 0.84977 | 0.45371 | 0.34834 | 0.279 | 0.26676 | 0.27016
| Velocity Head |  | Va²/2g | m | 0.036805 | 0.00753 | 0.030419 | 0.036805 | 0.036805 | 0.036805 | 0.036805 | 0.036805 | 0.010492 | 0.0061845 | 0.0039673 | 0.003627 | 0.00372
| Total Energy Level |  |  | masl | 2482.0368 | 2482.0075 | 2482.0304 | 2482.0368 | 2482.0368 | 2482.0368 | 2482.0368 | 2482.0368 | 2482.0105 | 2482.0062 | 2482.004 | 2482.0036 | 2482.0037 | 2482.0368 | 2482 |  | Ok
| Total water lelvel |  |  | masl | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482 | 2482
1 | HEADWORKS
1.1 | COARSE TRASHRACK
| Shape of bar | Rectangular
| Bar Thickness |  | t | mm | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Spacing between bars |  | b | mm | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| Number of Bars in each rack |  |  |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
| Rack Coefficient |  | Kt |  | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 |  |  |  |  | Rectangular | 2.42
| Rack inclination angle |  | Φ |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  |  |  |  | Round edge | 1.8
| Flow deviation angle |  | β |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  |  |  |  | Circular | 1.8
| Velocity through trashrack |  | Va | m/s | 0.84977 | 0.38437 | 0.77254 | 0.84977 | 0.84977 | 0.84977 | 0.84977 | 0.84977 | 0.45371 | 0.34834 | 0.279 | 0.26676 | 0.27016 |  |  |  |  | Pointed edge | 1.7
| Velocity Head |  | Va²/2g | m | 0.036805 | 0.00753 | 0.030419 | 0.036805 | 0.036805 | 0.036805 | 0.036805 | 0.036805 | 0.010492 | 0.0061845 | 0.0039673 | 0.003627 | 0.00372 |  |  |  |  | Rounded both edge | 1
[22 empty] | Streamlined | 0.8
| Headloss due to trashrack | [ ht = Kt (t/b)4/3 (Va2/2g) SinΦ ] | ht | m | 0.012023 | 0.0024599 | 0.0099373 | 0.012023 | 0.012023 | 0.012023 | 0.012023 | 0.012023 | 0.0034275 | 0.0020203 | 0.001296 | 0.0011849 | 0.0012152 |  |  |  | Ok
| Headloss due to flow deviation | [ hβ = (Va2/2g) Sinβ ] | hβ | m | 0.033357 | 0.0068245 | 0.027569 | 0.033357 | 0.033357 | 0.033357 | 0.033357 | 0.033357 | 0.009509 | 0.005605 | 0.0035956 | 0.0032871 | 0.0033714 |  |  |  | Ok
| Total Headloss | [ Headloss = ht + hβ ] |  | m | 0.04538 | 0.0092844 | 0.037506 | 0.04538 | 0.04538 | 0.04538 | 0.04538 | 0.04538 | 0.012936 | 0.0076254 | 0.0048917 | 0.004472 | 0.0045867 | 2481.9914 | 2481.9546 | 0.04538 | Ok | 2481.9546
| Total energy level |  |  |  | 2481.9914 | 2481.9982 | 2481.9929 | 2481.9914 | 2481.9914 | 2481.9914 | 2481.9914 | 2481.9914 | 2481.9976 | 2481.9986 | 2481.9991 | 2481.9992 | 2481.9991
| Total water level |  |  |  | 2481.9546 | 2481.9907 | 2481.9625 | 2481.9546 | 2481.9546 | 2481.9546 | 2481.9546 | 2481.9546 | 2481.9871 | 2481.9924 | 2481.9951 | 2481.9955 | 2481.9954
1.2 | INTAKE ORIFICE
| Intake invert level |  |  |  | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3 | 2479.3
| Coefficient of discharge |  | Cd |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
| No. of Openings |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Width |  |  | m | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
| Orifice Height |  |  | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 9.6
| Net Area of orifice |  |  | m² | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
| Velocity |  | Vo | m/s | 0.78125 | 0.35337 | 0.71025 | 0.78125 | 0.78125 | 0.78125 | 0.78125 | 0.78125 | 0.41713 | 0.32025 | 0.2565 | 0.24525 | 0.24837
| Velocity Head |  | Vo²/2g | m | 0.031109 | 0.0063646 | 0.025711 | 0.031109 | 0.031109 | 0.031109 | 0.031109 | 0.031109 | 0.0088682 | 0.0052273 | 0.0033533 | 0.0030656 | 0.0031442
| invert level of orifice |  |  | m
| Headloss through orifice | [ Headloss = (1/Cd²).Vo²/2g ] |  | m | 0.086413 | 0.01768 | 0.07142 | 0.086413 | 0.086413 | 0.086413 | 0.086413 | 0.086413 | 0.024634 | 0.01452 | 0.0093148 | 0.0085156 | 0.008734 | 2481.905 | 2481.8739 | 0.1261 | Ok | 2481.8682
| Total loss |  |  |  | 0.13179 | 0.026964 | 0.10893 | 0.13179 | 0.13179 | 0.13179 | 0.13179 | 0.13179 | 0.03757 | 0.022146 | 0.014206 | 0.012988 | 0.013321
| Total energy level |  |  |  | 2481.905 | 2481.9806 | 2481.9215 | 2481.905 | 2481.905 | 2481.905 | 2481.905 | 2481.905 | 2481.9729 | 2481.984 | 2481.9898 | 2481.9906 | 2481.9904
| Total water level |  |  |  | 2481.8739 | 2481.9742 | 2481.8958 | 2481.8739 | 2481.8739 | 2481.8739 | 2481.8739 | 2481.8739 | 2481.9641 | 2481.9788 | 2481.9864 | 2481.9876 | 2481.9873
1.3 | GATE LOSS
| Loss coefficient |  | Ke |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| No. of Openings |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Width |  |  | m | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
| Height |  |  | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Area of Canal |  |  | m² | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2
| Discharge |  |  | m³/s | 15 | 6.7848 | 13.6368 | 15 | 15 | 15 | 15 | 15 | 8.0088 | 6.1488 | 4.9248 | 4.7088 | 4.7688
| Velocity |  | Vg | m/s | 0.78125 | 0.35337 | 0.71025 | 0.78125 | 0.78125 | 0.78125 | 0.78125 | 0.78125 | 0.41713 | 0.32025 | 0.2565 | 0.24525 | 0.24837
| Velocity Head |  | Vg²/2g | m | 0.031109 | 0.0063646 | 0.025711 | 0.031109 | 0.031109 | 0.031109 | 0.031109 | 0.031109 | 0.0088682 | 0.0052273 | 0.0033533 | 0.0030656 | 0.0031442
| Headloss through gate | [ hg = Kg.V2²/2g ] |  | m | 0.0062217 | 0.0012729 | 0.0051423 | 0.0062217 | 0.0062217 | 0.0062217 | 0.0062217 | 0.0062217 | 0.0017736 | 0.0010455 | 0.00067067 | 0.00061313 | 0.00062885 | 2481.8988 | 2481.8677
Water level at inlet of Gravel Trap
| Total Energy level |  |  |  | 2481.8988 | 2481.9793 | 2481.9164 | 2481.8988 | 2481.8988 | 2481.8988 | 2481.8988 | 2481.8988 | 2481.9711 | 2481.983 | 2481.9891 | 2481.99 | 2481.9898
| Total water level |  |  |  | 2481.8677 | 2481.9729 | 2481.8906 | 2481.8677 | 2481.8677 | 2481.8677 | 2481.8677 | 2481.8677 | 2481.9623 | 2481.9778 | 2481.9857 | 2481.987 | 2481.9866
1.4 | GRAVEL TRAP
| Manning's Coefficient for hardstone lining |  |  |  | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018 | 0.018
| Length |  | Lg | m | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4
| Top Width |  |  | m | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
| Water Depth |  |  | m | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 2.5677 | 5.4
| No. of Hoppers |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Width of Divide wall |  |  | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Top width of Hopper |  |  | m | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
| Bottom Width of Hopper |  |  | m | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
| Hopper Depth |  |  | m | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Hopper Side Slope Horizontal Length |  |  | m | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | 18.6103
| Average Cross Sectional Area |  |  | m² | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931 | 43.931
| Wetted Perimeter |  |  | m | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354 | 18.9354
| Hydraulic Radius |  | Rg | m | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32 | 2.32
Longitudinal Bed slope
| Bed Slope |  |  | m/m | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.5 | 0.5 | 0.5 | 0.5
| Velocity in gravel trap |  | Vg | m/s | 0.34144 | 0.15444 | 0.31041 | 0.34144 | 0.34144 | 0.34144 | 0.34144 | 0.34144 | 0.1823 | 0.13997 | 0.1121 | 0.10719 | 0.10855
| Velocity Head in gravel trap |  | Vg²/2g | m | 0.0059421 | 0.0012157 | 0.0049112 | 0.0059421 | 0.0059421 | 0.0059421 | 0.0059421 | 0.0059421 | 0.0016939 | 0.00099848 | 0.00064053 | 0.00058557 | 0.00060059
| Friction Loss | [ hf = n².Vg².Lg/Rg4/3 ] | hf | m | 0.00011561 | 2.3652e-05 | 9.5549e-05 | 0.00011561 | 0.00011561 | 0.00011561 | 0.00011561 | 0.00011561 | 3.2956e-05 | 1.9426e-05 | 1.2462e-05 | 1.1393e-05 | 1.1685e-05
| Contraction Loss | [ hC = KL.V2²/2g ] | hC | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | #REF!
| Total Headloss | [ Headloss = hf + hC ] |  | m | 0.00011561 | 2.3652e-05 | 9.5549e-05 | 0.00011561 | 0.00011561 | 0.00011561 | 0.00011561 | 0.00011561 | 3.2956e-05 | 1.9426e-05 | 1.2462e-05 | 1.1393e-05 | 1.1685e-05 | 2481.8987 | 2481.8927 | #REF! | 1013.8638
| Total Energy level |  |  |  | 2481.8987 | 2481.9793 | 2481.9163 | 2481.8987 | 2481.8987 | 2481.8987 | 2481.8987 | 2481.8987 | 2481.9711 | 2481.983 | 2481.9891 | 2481.99 | 2481.9898
| Total water level |  |  |  | 2481.8927 | 2481.9781 | 2481.9113 | 2481.8927 | 2481.8927 | 2481.8927 | 2481.8927 | 2481.8927 | 2481.9694 | 2481.982 | 2481.9884 | 2481.9894 | 2481.9892
TRANSITION TO APPROACH CULVERT
| Invert Level |  |  | masl | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31 | 2476.31
| Average Width |  | Wavg | m | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
| Water Depth |  |  | m | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06 | 5.06
| Average velocity |  | Vavg | m/s | 0.35291 | 0.15963 | 0.32084 | 0.35291 | 0.35291 | 0.35291 | 0.35291 | 0.35291 | 0.18842 | 0.14466 | 0.11587 | 0.11078 | 0.1122
| Contraction loss coefficient |  | Kc |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Velocity d/s to contraction |  | V2 | m/s | 1.5278 | 0.69104 | 1.3889 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 0.81571 | 0.62627 | 0.5016 | 0.4796 | 0.48571
| Velocity head |  | Vg²/2g | m | 0.11262 | 0.023041 | 0.093079 | 0.11262 | 0.11262 | 0.11262 | 0.11262 | 0.11262 | 0.032104 | 0.018924 | 0.01214 | 0.011098 | 0.011383
| Contraction headloss | [ hc = Kc.V2²/2g ] | hc | m | 0.033785 | 0.0069123 | 0.027924 | 0.033785 | 0.033785 | 0.033785 | 0.033785 | 0.033785 | 0.0096312 | 0.0056771 | 0.0036419 | 0.0033294 | 0.0034148
| Energy Level |  |  | masl | 2481.8649 | 2481.9724 | 2481.8883 | 2481.8649 | 2481.8649 | 2481.8649 | 2481.8649 | 2481.8649 | 2481.9615 | 2481.9773 | 2481.9854 | 2481.9867 | 2481.9863
| Water level |  |  | masl | 2481.7523 | 2481.9493 | 2481.7953 | 2481.7523 | 2481.7523 | 2481.7523 | 2481.7523 | 2481.7523 | 2481.9294 | 2481.9584 | 2481.9733 | 2481.9756 | 2481.975
Culvert inlet Fine Trashrack
| Width of opening |  |  | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Number |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Height |  |  | m | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
| Shape of bar | Rectangular
| Bar Thickness |  | t | mm | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Spacing between bars |  | b | mm | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Number of Bars in each rack |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
| Net width |  |  | m | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
| Rack Coefficient |  | Kt |  | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 |  |  |  |  | Rectangular | 2.42
| Rack inclination angle |  | Φ |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  |  |  |  | Round edge | 1.8
| Flow deviation angle |  | β |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Circular | 1.8
| Velocity through trashrack |  | Va | m/s | 4.4014 | 1.9908 | 4.0014 | 4.4014 | 4.4014 | 4.4014 | 4.4014 | 4.4014 | 2.35 | 1.8042 | 1.4451 | 1.3817 | 1.3993 |  |  |  |  | Pointed edge | 1.7
| Velocity Head |  | Va²/2g | m | 0.98738 | 0.20201 | 0.81607 | 0.98738 | 0.98738 | 0.98738 | 0.98738 | 0.98738 | 0.28147 | 0.16591 | 0.10643 | 0.097302 | 0.099798 |  |  |  |  | Rounded both edge | 1
[22 empty] | Streamlined | 0.8
| Headloss due to trashrack | [ ht = Kt (t/b)4/3 (Va2/2g) SinΦ ] | ht | m | 0.99826 | 0.20424 | 0.82506 | 0.99826 | 0.99826 | 0.99826 | 0.99826 | 0.99826 | 0.28457 | 0.16774 | 0.10761 | 0.098374 | 0.1009 |  |  |  | Ok
| Headloss due to flow deviation | [ hβ = (Va2/2g) Sinβ ] | hβ | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Ok
| Total Headloss | [ Headloss = ht + hβ ] |  | m | 0.99826 | 0.20424 | 0.82506 | 0.99826 | 0.99826 | 0.99826 | 0.99826 | 0.99826 | 0.28457 | 0.16774 | 0.10761 | 0.098374 | 0.1009 | -0.99826 | -1.9856 | 2483.9856 | Ok | -0.99826
| Total energy level |  |  |  | 2480.8666 | 2481.7681 | 2481.0633 | 2480.8666 | 2480.8666 | 2480.8666 | 2480.8666 | 2480.8666 | 2481.6769 | 2481.8096 | 2481.8778 | 2481.8883 | 2481.8854
| Total water level |  |  |  | 2479.8793 | 2481.5661 | 2480.2472 | 2479.8793 | 2479.8793 | 2479.8793 | 2479.8793 | 2479.8793 | 2481.3954 | 2481.6436 | 2481.7714 | 2481.791 | 2481.7856
1.5 | APPROACH CULVERT | [20 empty] | 1986.6784
| Manning's Coefficient |  |  | n | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
| Number of canal |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Discharge per canal |  | Qc | m³/s | 6.875 | 3.1097 | 6.2502 | 6.875 | 6.875 | 6.875 | 6.875 | 6.875 | 3.6707 | 2.8182 | 2.2572 | 2.1582 | 2.1857
| Width |  |  | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Water Depth |  |  | m | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25
| Length |  | Lc | m | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58 | 21.58
| Cross Sectional Area |  |  | m² | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
| Wetted Perimeter |  |  | m | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| Hydraulic Radius |  | Rc | m | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 | 0.69231 |  |  |  | 0.69231
| Discharge to be passed through canal |  |  |  | 13.75 | 6.2194 | 12.5004 | 13.75 | 13.75 | 13.75 | 13.75 | 13.75 | 7.3414 | 5.6364 | 4.5144 | 4.3164 | 4.3714
| No of feeder canals |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Discharge per canal |  |  |  | 6.875 | 3.1097 | 6.2502 | 6.875 | 6.875 | 6.875 | 6.875 | 6.875 | 3.6707 | 2.8182 | 2.2572 | 2.1582 | 2.1857
| Velocity |  | Vc | m/s | 1.5278 | 0.69104 | 1.3889 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 0.81571 | 0.62627 | 0.5016 | 0.4796 | 0.48571 |  |  |  | 0.32871
| Area |  |  | m² | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 |  |  |  | 9
| Velocity Head |  | Vc²/2g | m | 0.11897 | 0.02434 | 0.098325 | 0.11897 | 0.11897 | 0.11897 | 0.11897 | 0.11897 | 0.033914 | 0.01999 | 0.012824 | 0.011724 | 0.012024
| Headloss (Friction Loss) | [ hf = n².VT².LT/RT4/3 ] |  | m | 0.018505 | 0.003786 | 0.015294 | 0.018505 | 0.018505 | 0.018505 | 0.018505 | 0.018505 | 0.0052752 | 0.0031095 | 0.0019947 | 0.0018236 | 0.0018704 | 2481.8802 | 2481.7612 | 0.2388 | 0.018505 | CHECK, whether canal invert has to be lowered down in order to ensure ease of flow during low flow.
| Total Energy level |  | masl |  | 2480.8481 | 2481.7643 | 2481.048 | 2480.8481 | 2480.8481 | 2480.8481 | 2480.8481 | 2480.8481 | 2481.6716 | 2481.8064 | 2481.8758 | 2481.8865 | 2481.8836
| Total water level |  | masl |  | 2480.7292 | 2481.74 | 2480.9497 | 2480.7292 | 2480.7292 | 2480.7292 | 2480.7292 | 2480.7292 | 2481.6377 | 2481.7865 | 2481.863 | 2481.8748 | 2481.8716
| total energy level |  |  | masl | 2480.8481 | 2481.7643 | 2481.048 | 2480.8481 | 2480.8481 | 2480.8481 | 2480.8481 | 2480.8481 | 2481.6716 | 2481.8064 | 2481.8758 | 2481.8865 | 2481.8836
| Total water level |  |  | masl | 2480.7292 | 2481.74 | 2480.9497 | 2480.7292 | 2480.7292 | 2480.7292 | 2480.7292 | 2480.7292 | 2481.6377 | 2481.7865 | 2481.863 | 2481.8748 | 2481.8716
1.6 | GATE LOSS
| Loss coefficient |  | Ke |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| No. of Openings |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Width |  |  | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Height |  |  | m | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25
| Area of Canal |  |  | m² | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
| Discharge |  |  | m³/s | 6.875 | 3.1097 | 6.2502 | 6.875 | 6.875 | 6.875 | 6.875 | 6.875 | 3.6707 | 2.8182 | 2.2572 | 2.1582 | 2.1857
| Velocity |  | Vg | m/s | 1.5278 | 0.69104 | 1.3889 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 0.81571 | 0.62627 | 0.5016 | 0.4796 | 0.48571
| Velocity Head |  | Vg²/2g | m | 0.11897 | 0.02434 | 0.098325 | 0.11897 | 0.11897 | 0.11897 | 0.11897 | 0.11897 | 0.033914 | 0.01999 | 0.012824 | 0.011724 | 0.012024
| Headloss through gate | [ hg = Kg.V2²/2g ] |  | m | 0.023793 | 0.0048679 | 0.019665 | 0.023793 | 0.023793 | 0.023793 | 0.023793 | 0.023793 | 0.0067827 | 0.0039981 | 0.0025648 | 0.0023447 | 0.0024048 | 2481.8564 | 2481.7374
Water level at inlet of approach culvert
| Total Energy level |  |  | masl | 2480.8243 | 2481.7595 | 2481.0283 | 2480.8243 | 2480.8243 | 2480.8243 | 2480.8243 | 2480.8243 | 2481.6649 | 2481.8024 | 2481.8733 | 2481.8841 | 2481.8812
| Total water level |  |  | masl | 2480.7054 | 2481.7351 | 2480.93 | 2480.7054 | 2480.7054 | 2480.7054 | 2480.7054 | 2480.7054 | 2481.6309 | 2481.7825 | 2481.8604 | 2481.8724 | 2481.8691
1.7 | SETTLING BASIN
| No. of bays |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Discharge per bay |  |  | m³/s | 6.875 | 3.1097 | 6.2502 | 6.875 | 6.875 | 6.875 | 6.875 | 6.875 | 3.6707 | 2.8182 | 2.2572 | 2.1582 | 2.1857
| Manning's Coefficient |  |  | n | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
Expansion loss coeficeint, ASCE
1.7.1 | INLET TRANSITION
| Inlet transition angle |  | α | degree | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  |  |  | α |  | 2 | 5 | 10 | 12 | 15 | 20 | 25 | 30 | 40 | 50 | 60
| Expansion loss coeffcient |  | Ke |  | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 |  |  |  |  | Ke | Low | 0.02 | 0.04 | 0.08 | 0.1 | 0.16 | 0.31 | 0.4 | 0.49 | 0.6 | 0.67 | 0.72
| Inlet transition Length |  | Li | m | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | 21.81 | [5 empty] | High value | 0.03 | 0.12 | 0.16 | 0.2 | 0.27 | 0.4 | 0.55 | 0.66 | 0.9 | 1 | 1.1
| Average Width |  | WT | m | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
| Average Height |  | HT | m | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84 | 5.84
| Average Area |  | AT | m² | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | 37.96 | [8 empty] | 0.6
| Wetted Perimeter |  | PT | m | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | 18.18 | [8 empty] | 4.2
| Bed Slope |  |  |  | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448 | 0.2448
| water height in canal |  |  | m | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25
| Normal water level at inlet |  |  | m | 2480.7054 | 2481.7351 | 2480.93 | 2480.7054 | 2480.7054 | 2480.7054 | 2480.7054 | 2480.7054 | 2481.6309 | 2481.7825 | 2481.8604 | 2481.8724 | 2481.8691
| Canal invert level at start |  |  | m | 2478.4554 | 2479.4851 | 2478.68 | 2478.4554 | 2478.4554 | 2478.4554 | 2478.4554 | 2478.4554 | 2479.3809 | 2479.5325 | 2479.6104 | 2479.6224 | 2479.6191
| Canal invert level at end |  |  |  | 2473.1726 | 2474.2023 | 2473.3972 | 2473.1726 | 2473.1726 | 2473.1726 | 2473.1726 | 2473.1726 | 2474.0982 | 2474.2497 | 2474.3277 | 2474.3396 | 2474.3364
| Hydraulic Radius |  | RT | m | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | 2.088 | [8 empty] | 0.2
| Bed Slope |  |  | m/m | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727 | 0.22727
| Velocity |  | VT | m/s | 0.18111 | 0.08192 | 0.16465 | 0.18111 | 0.18111 | 0.18111 | 0.18111 | 0.18111 | 0.096699 | 0.074241 | 0.059463 | 0.056855 | 0.057579 | [8 empty] | 5
| Velocity Head |  | VT²/2g | m | 0.0016718 | 0.00034205 | 0.0013818 | 0.0016718 | 0.0016718 | 0.0016718 | 0.0016718 | 0.0016718 | 0.00047659 | 0.00028093 | 0.00018021 | 0.00016475 | 0.00016898 | [5 empty] | 591.5
4.2
| Transition Loss | [ ht = Ke. (V1-V2)²/2g ] | ht | m | 0.053319 | 0.010909 | 0.044068 | 0.053319 | 0.053319 | 0.053319 | 0.053319 | 0.053319 | 0.0152 | 0.0089595 | 0.0057475 | 0.0052544 | 0.0053891 | [5 empty] | 0.2 |  | 6.4 |  | 7.45
| Friction Loss | [ hf = n².VT².LT/RT4/3 ] | hf | m | 6.0314e-05 | 1.234e-05 | 4.985e-05 | 6.0314e-05 | 6.0314e-05 | 6.0314e-05 | 6.0314e-05 | 6.0314e-05 | 1.7194e-05 | 1.0135e-05 | 6.5015e-06 | 5.9437e-06 | 6.0962e-06 | [5 empty] | 2 |  | 585.1 |  | 584.05
| Total Headloss | [ Headloss = ht + hf ] |  | m | 0.05338 | 0.010921 | 0.044118 | 0.05338 | 0.05338 | 0.05338 | 0.05338 | 0.05338 | 0.015217 | 0.0089696 | 0.005754 | 0.0052603 | 0.0053952 | 2481.803 | 2481.8013 | 0.19867
| Total Energy level |  |  | masl | 2480.771 | 2481.7485 | 2480.9842 | 2480.771 | 2480.771 | 2480.771 | 2480.771 | 2480.771 | 2481.6496 | 2481.7935 | 2481.8675 | 2481.8789 | 2481.8758
| Total water level |  |  | masl | 2480.7693 | 2481.7482 | 2480.9828 | 2480.7693 | 2480.7693 | 2480.7693 | 2480.7693 | 2480.7693 | 2481.6492 | 2481.7932 | 2481.8673 | 2481.8787 | 2481.8756
1.7.2 | MAIN SECTION
| Length |  | Ls | m | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
| No of bay |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Width of bay at top (assume) |  |  | m | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
| thickness of divide wall at bottom |  |  | m | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Water Width |  |  | m | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
| Water Depth |  |  | m | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205
| discharge per bay |  |  | m^3/s | 6.875 | 3.1097 | 6.2502 | 6.875 | 6.875 | 6.875 | 6.875 | 6.875 | 3.6707 | 2.8182 | 2.2572 | 2.1582 | 2.1857
| constant a |  |  |  | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
| Camp's critical velocity |  |  |  | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041 | 0.17041
| min depth of water required |  |  |  | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205
| Cross Sectional Area of Flow |  | As | m² | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255 | 46.255
| Adopt depth |  | Hw |  | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205 | 4.205
| Wetted Perimeter |  | Ps | m | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41 | 19.41
| Hydraulic Radius |  | Rs | m | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383 | 2.383
| Bed Slope |  |  | m/m | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025
| Velocity |  | Vs | m/s | 0.14863 | 0.067229 | 0.13512 | 0.14863 | 0.14863 | 0.14863 | 0.14863 | 0.14863 | 0.079358 | 0.060927 | 0.048799 | 0.046659 | 0.047253
| Velocity Head |  | Vs²/2g | m | 0.001126 | 0.00023037 | 0.00093062 | 0.001126 | 0.001126 | 0.001126 | 0.001126 | 0.001126 | 0.00032098 | 0.0001892 | 0.00012137 | 0.00011096 | 0.00011381
| Headloss (Friction Loss) | [ Headloss = n².Vs².Ls/Rs4/3 ] |  | m | 0.00013273 | 2.7157e-05 | 0.00010971 | 0.00013273 | 0.00013273 | 0.00013273 | 0.00013273 | 0.00013273 | 3.7839e-05 | 2.2304e-05 | 1.4308e-05 | 1.308e-05 | 1.3416e-05 | 2481.8029 | 2481.8017 | 0.19826
| total energy level |  |  | masl | 2480.7708 | 2481.7485 | 2480.9841 | 2480.7708 | 2480.7708 | 2480.7708 | 2480.7708 | 2480.7708 | 2481.6496 | 2481.7935 | 2481.8675 | 2481.8789 | 2481.8758
| Total water level |  |  | masl | 2480.7697 | 2481.7483 | 2480.9832 | 2480.7697 | 2480.7697 | 2480.7697 | 2480.7697 | 2480.7697 | 2481.6493 | 2481.7933 | 2481.8674 | 2481.8788 | 2481.8756
1.7.3 | OUTLET ORIFICE
| Coefficient of discharge |  | Cd |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
| No of Gates |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Width of the Gate |  |  | m | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05 | 4.05
| Height |  |  | m | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Area of orifice |  |  | m² | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3
| Total discharge |  |  | m³/s | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974
| Velocity |  | Vo | m/s | 0.5144 | 0.23267 | 0.46765 | 0.5144 | 0.5144 | 0.5144 | 0.5144 | 0.5144 | 0.27465 | 0.21086 | 0.16889 | 0.16148 | 0.16354
| Velocity Head |  | Vo²/2g | m | 0.013487 | 0.0027593 | 0.011147 | 0.013487 | 0.013487 | 0.013487 | 0.013487 | 0.013487 | 0.0038447 | 0.0022662 | 0.0014538 | 0.0013291 | 0.0013632
| Headloss through orifice | [ Headloss = (1/Cd²).Vo²/2g ] |  | m | 0.037463 | 0.0076647 | 0.030963 | 0.037463 | 0.037463 | 0.037463 | 0.037463 | 0.037463 | 0.01068 | 0.0062951 | 0.0040383 | 0.0036918 | 0.0037865 | 2481.7654 | 2481.7519 | 0.24809
| total energy level |  |  | masl | 2480.7334 | 2481.7409 | 2480.9531 | 2480.7334 | 2480.7334 | 2480.7334 | 2480.7334 | 2480.7334 | 2481.6389 | 2481.7872 | 2481.8635 | 2481.8752 | 2481.872
| Total water level |  |  | masl | 2480.7199 | 2481.7381 | 2480.942 | 2480.7199 | 2480.7199 | 2480.7199 | 2480.7199 | 2480.7199 | 2481.6351 | 2481.7849 | 2481.862 | 2481.8738 | 2481.8706
1.8 | HEADPOND/FOREBAY
| Manning's Coefficient |  |  | n | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
| Average Width |  |  | m | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4
| Water Depth |  |  | m | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 | 8.66 |  |  |  |  | Check submergence
| Length |  | Lh | m | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85 | 10.85
| Cross Sectional Area |  |  | m² | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984 | 193.984
| Wetted Perimeter |  |  | m | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72
| Hydraulic Radius |  | Rh | m | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838 | 4.8838
| Energy Slope |  |  | m/m | 1.1275e-07 | 2.3069e-08 | 9.319e-08 | 1.1275e-07 | 1.1275e-07 | 1.1275e-07 | 1.1275e-07 | 1.1275e-07 | 3.2143e-08 | 1.8946e-08 | 1.2154e-08 | 1.1111e-08 | 1.1396e-08 | [5 empty] | 7.0686
| Velocity |  | Vh | m/s | 0.064438 | 0.029147 | 0.058582 | 0.064438 | 0.064438 | 0.064438 | 0.064438 | 0.064438 | 0.034405 | 0.026415 | 0.021156 | 0.020228 | 0.020486 | [5 empty] | 3.5343
| Velocity Head |  | Vh²/2g | m | 0.00021164 | 4.3299e-05 | 0.00017492 | 0.00021164 | 0.00021164 | 0.00021164 | 0.00021164 | 0.00021164 | 6.0331e-05 | 3.5562e-05 | 2.2813e-05 | 2.0856e-05 | 2.1391e-05 | [5 empty] | 8.0343
| Coefficient of Contraction |  | KL |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [5 empty] | 0.758
| Headloss (Friction Loss) | [ hH = n².Vh².Lh/Rh4/3 ] | hH | m | 1.2234e-06 | 2.5029e-07 | 1.0111e-06 | 1.2234e-06 | 1.2234e-06 | 1.2234e-06 | 1.2234e-06 | 1.2234e-06 | 3.4875e-07 | 2.0557e-07 | 1.3187e-07 | 1.2056e-07 | 1.2365e-07
| Contraction Loss | [ hC = KL.V2²/2g ] | hC | m | 0.034964 | 0.0071535 | 0.028898 | 0.034964 | 0.034964 | 0.034964 | 0.034964 | 0.034964 | 0.0099673 | 0.0058752 | 0.0037689 | 0.0034456 | 0.0035339
| Total Headloss | [ Headloss = hH + hC] |  | m | 0.034966 | 0.0071537 | 0.028899 | 0.034966 | 0.034966 | 0.034966 | 0.034966 | 0.034966 | 0.0099676 | 0.0058754 | 0.0037691 | 0.0034457 | 0.0035341 | 2481.7304 | 2481.7302 | 0.26978
| total energy level |  |  | masl | 2480.6984 | 2481.7337 | 2480.9242 | 2480.6984 | 2480.6984 | 2480.6984 | 2480.6984 | 2480.6984 | 2481.629 | 2481.7813 | 2481.8597 | 2481.8717 | 2481.8684
| Total water level |  |  | masl | 2480.6982 | 2481.7337 | 2480.924 | 2480.6982 | 2480.6982 | 2480.6982 | 2480.6982 | 2480.6982 | 2481.6289 | 2481.7812 | 2481.8597 | 2481.8717 | 2481.8684
Culvert inlet Fine Trashrack
| Width of opening |  |  | m | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
| Number |  |  |  | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Height |  |  | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Shape of bar | Rectangular
| Bar Thickness |  | t | mm | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Spacing between bars |  | b | mm | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Number of Bars in each rack |  |  |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
| Net width |  |  | m | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71
| Rack Coefficient |  | Kt |  | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 | 2.42 |  |  |  |  | Rectangular | 2.42
| Rack inclination angle |  | Φ |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  |  |  |  | Round edge | 1.8
| Flow deviation angle |  | β |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Circular | 1.8
| Velocity through trashrack |  | Va | m/s | 3.655 | 1.6532 | 3.3228 | 3.655 | 3.655 | 3.655 | 3.655 | 3.655 | 1.9515 | 1.4982 | 1.2 | 1.1474 | 1.162 |  |  |  |  | Pointed edge | 1.7
| Velocity Head |  | Va²/2g | m | 0.68088 | 0.1393 | 0.56274 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.1941 | 0.11441 | 0.073394 | 0.067098 | 0.068818 |  |  |  |  | Rounded both edge | 1
[22 empty] | Streamlined | 0.8
| Headloss due to trashrack | [ ht = Kt (t/b)4/3 (Va2/2g) SinΦ ] | ht | m | 0.70183 | 0.14359 | 0.58006 | 0.70183 | 0.70183 | 0.70183 | 0.70183 | 0.70183 | 0.20007 | 0.11793 | 0.075653 | 0.069163 | 0.070936 |  |  |  | Ok
| Headloss due to flow deviation | [ hβ = (Va2/2g) Sinβ ] | hβ | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | Ok
| Total Headloss | [ Headloss = ht + hβ ] |  | m | 0.70183 | 0.14359 | 0.58006 | 0.70183 | 0.70183 | 0.70183 | 0.70183 | 0.70183 | 0.20007 | 0.11793 | 0.075653 | 0.069163 | 0.070936 | -0.70183 | -1.3827 | 2483.3827 | Ok | -0.70183
| Total energy level |  |  |  | 2479.9966 | 2481.5901 | 2480.3442 | 2479.9966 | 2479.9966 | 2479.9966 | 2479.9966 | 2479.9966 | 2481.4289 | 2481.6634 | 2481.784 | 2481.8026 | 2481.7975
| Total water level |  |  |  | 2479.3157 | 2481.4508 | 2479.7814 | 2479.3157 | 2479.3157 | 2479.3157 | 2479.3157 | 2479.3157 | 2481.2348 | 2481.5489 | 2481.7106 | 2481.7355 | 2481.7287
| TOTAL HEADLOSS IN HEADWORKS |  |  |  | 2.0402 | 0.41742 | 1.6863 | 2.0402 | 2.0402 | 2.0402 | 2.0402 | 2.0402 | 0.58161 | 0.34283 | 0.21993 | 0.20106 | 0.20621
| Velocity at approach canal |  |  |  | 1.5278 | 0.69104 | 1.3889 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 1.5278 | 0.81571 | 0.62627 | 0.5016 | 0.4796 | 0.48571
| TOTAL HEADLOSS COEFFICIENT FOR HEADWORKS |  |  |  | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499 | 17.1499
[5 empty] | 2479.9966 | 2481.5901 | 2480.3442 | 2479.9966 | 2479.9966 | 2479.9966 | 2479.9966 | 2479.9966 | 2481.4289 | 2481.6634 | 2481.784 | 2481.8026 | 2481.7975
2 | WATERWAY
2 | HEADRACE PIPE | [20 empty] | Reference: Guidelines for design of Intake
| k | Roughness height |  | mm | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
| k/D |  |  |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
| Re | ud/v |  |  | 7237984.945 | 3273885.3503 | 6580196.8732 | 7237984.945 | 7237984.945 | 7237984.945 | 7237984.945 | 7237984.945 | 3864504.9218 | 2966994.7887 | 2376375.2171 | 2272148.2339 | 2301100.1737
| Friction Factor for Headrace Pipe |  | f |  | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
| Design discharge |  | Q | m3/s | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974 |  |  |  |  | Description | Structure | Manning's Value, n
| Length of Pipe |  | Lc | m | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 | 422.3 |  |  |  |  | Hard stone lined surface | Gravel Trap | 0.018
| Pipe Diameter |  | d | m | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 |  |  |  |  | Concrete Surface | Approach Culvert | 0.015
| Pipe Area |  | Ac | m2 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 | 3.7994 |  |  |  |  | Concrete Lined Surface | Settling Basin | 0.016
| Flow Velocity in Pipe |  | Vp | m/s | 3.29 | 1.4881 | 2.991 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 1.7566 | 1.3486 | 1.0802 | 1.0328 | 1.046 |  |  |  |  | Concrete Lined Surface | Feeding Tunnel | 0.016
| Velocity Head |  | Vp²/2g | m | 0.55168 | 0.11287 | 0.45597 | 0.55168 | 0.55168 | 0.55168 | 0.55168 | 0.55168 | 0.15727 | 0.092702 | 0.059468 | 0.054366 | 0.055761
| Headloss | [ Headloss = (f.L.v2)/2.g.d] | Hp | m | 1.3767 | 0.28166 | 1.1378 | 1.3767 | 1.3767 | 1.3767 | 1.3767 | 1.3767 | 0.39245 | 0.23133 | 0.1484 | 0.13567 | 0.13915 | #REF! | #REF!
Bend Loss in HRP
Bend 1
| Bend radius |  | R | m | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| Rb/D |  | Rb/D |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Bend angle |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Bend Coefficient |  |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Total bend loss in tunnel |  |  | m | 0.027584 | 0.0056436 | 0.022798 | 0.027584 | 0.027584 | 0.027584 | 0.027584 | 0.027584 | 0.0078635 | 0.0046351 | 0.0029734 | 0.0027183 | 0.002788
Bend 2
| Bend radius |  | R | m | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| Rb/D |  | Rb/D |  | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36
| Bend angle |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Bend Coefficient |  |  |  | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036 | 0.036
| Total bend loss in tunnel |  |  | m | 0.019861 | 0.0040634 | 0.016415 | 0.019861 | 0.019861 | 0.019861 | 0.019861 | 0.019861 | 0.0056617 | 0.0033373 | 0.0021409 | 0.0019572 | 0.0020074
Bend 3
| Bend radius |  | R | m | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| Rb/D |  | Rb/D |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
| Bend angle |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Bend Coefficient |  |  |  | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075
| Total bend loss in tunnel |  |  | m | 0.041376 | 0.0084653 | 0.034198 | 0.041376 | 0.041376 | 0.041376 | 0.041376 | 0.041376 | 0.011795 | 0.0069527 | 0.0044601 | 0.0040775 | 0.004182
Bend 4
| Bend radius |  | R | m | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| Rb/D |  | Rb/D |  | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
| Bend angle |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Bend Coefficient |  |  |  | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075
| Total bend loss in tunnel |  |  | m | 0.041376 | 0.0084653 | 0.034198 | 0.041376 | 0.041376 | 0.041376 | 0.041376 | 0.041376 | 0.011795 | 0.0069527 | 0.0044601 | 0.0040775 | 0.004182
| TOTAL Bend loss in HRP |  |  |  | 0.1302 | 0.026638 | 0.10761 | 0.1302 | 0.1302 | 0.1302 | 0.1302 | 0.1302 | 0.037116 | 0.021878 | 0.014035 | 0.01283 | 0.013159
| Total Headloss in HRP |  |  |  | 1.5069 | 0.3083 | 1.2454 | 1.5069 | 1.5069 | 1.5069 | 1.5069 | 1.5069 | 0.42957 | 0.25321 | 0.16243 | 0.1485 | 0.1523
| total energy level |  |  |  | 2478.4897 | 2481.2818 | 2479.0987 | 2478.4897 | 2478.4897 | 2478.4897 | 2478.4897 | 2478.4897 | 2480.9993 | 2481.4101 | 2481.6216 | 2481.6541 | 2481.6452
| Total water level |  |  |  | 2477.938 | 2481.1689 | 2478.6428 | 2477.938 | 2477.938 | 2477.938 | 2477.938 | 2477.938 | 2480.842 | 2481.3174 | 2481.5621 | 2481.5997 | 2481.5894
2.1 | HEADRACE TUNNEL
| Design Discharge |  | Q | m3/s | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974
| Manning's coefficient for shotcrete tunnel |  | n |  | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027 | 0.027
| Manning's coefficient for concrete lined tunnel |  | n |  | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
| Total length from inlet portal to surge shaft |  | m |  | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110 | 6110
| Shotcrete linned length |  | Ls | m | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110 | 5110
| Concrete linned length |  | Lc | m | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Diameter concrete lined |  | dt | m | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
| Diameter shotcrete lined |  |  | m | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
| height of rectangular portion(shotcrete) |  |  | m | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
| height of rectangular portion(concrete) |  |  |  | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85
| Concrete lined portion | [16 empty] | #REF!
| Sectional area | [ A = D2/2 +pi().D2/8] | At | m2 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588 | 8.2588
| Flow velocity in tunnel |  | Vts | m/s | 1.5135 | 0.68461 | 1.376 | 1.5135 | 1.5135 | 1.5135 | 1.5135 | 1.5135 | 0.80811 | 0.62043 | 0.49693 | 0.47513 | 0.48119 |  |  |  |  | Reference : Guidelines for the design of Intake for Hydroelectric Plants
| Wetted perimeter | [D+2.D/2+(pi () D/2)] | Pt | m | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 | 10.9982 |  |  |  |  | Page No: 63; Table 3.5
| Hydraulic radius |  | R | m | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | 0.75092 | [5 empty] | Bend Loss Coefficient (K)
| Shotcrete lined portion | [20 empty] | Angle ( ° ) | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120
| Sectional area |  | At |  | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 | 10.1012 |  |  |  |  | Ke | 0.2 | 0.36 | 0.5 | 0.63 | 0.74 | 0.82 | 0.89 | 0.95 | 1 | 1.05 | 1.09 | 1.12
| Flow velocity in tunnel |  | Vtc |  | 1.2375 | 0.55973 | 1.125 | 1.2375 | 1.2375 | 1.2375 | 1.2375 | 1.2375 | 0.66071 | 0.50726 | 0.40629 | 0.38847 | 0.39342
| Wetted perimeter |  | Pt |  | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 | 12.0265 |  |  |  |  | For Contraction Designed to meet angular changes:
| Hydraulic radius |  | R |  | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 | 0.83991 |  |  |  |  | tanα=C√(gd)/U
| Headloss | [ HL = (Q/A)2. n²Lt/Rt4/3 ] | [19 empty] | U=average velocities
| Shotcrete lined portion |  | Hu | m | 12.503 | [16 empty] | d=average dia
| Concrete lined portion |  | HL | m | 0.43479 | [16 empty] | α=angle of conduit wall surface with respect to centre line
#REF!
| Total Headloss | [ Headloss = Hu+ HL] |  | m | 12.9378 | [16 empty] | #REF! | Bend Loss Coefficient (K) 10: average velocity
[22 empty] | 4.45 | Bend Loss Coefficient (K) 10: average dia
| Headloss (Friction Loss) - Shotcrete lined | [ hf = n².VT².LT/RT4/3 ] | hlsl | m | 7.1985 | 1.4728 | 5.9495 | 7.1985 | 7.1985 | 7.1985 | 7.1985 | 7.1985 | 2.0521 | 1.2096 | 0.77595 | 0.70938 | 0.72757
| Headloss (Friction Loss) - Concrete lined | [ hf = n².VT².LT/RT4/3 ] | hlcl | m | 0.75518 | 0.1545 | 0.62415 | 0.75518 | 0.75518 | 0.75518 | 0.75518 | 0.75518 | 0.21528 | 0.1269 | 0.081404 | 0.07442 | 0.076328
| Total Headloss |  |  | m | 7.9537 | 1.6273 | 6.5737 | 7.9537 | 7.9537 | 7.9537 | 7.9537 | 7.9537 | 2.2674 | 1.3365 | 0.85736 | 0.7838 | 0.8039
| Velocity Head (shotcrete Lined) |  |  | m | 0.07805 | 0.015968 | 0.064508 | 0.07805 | 0.07805 | 0.07805 | 0.07805 | 0.07805 | 0.02225 | 0.013115 | 0.0084133 | 0.0076915 | 0.0078887 | #REF! | #REF!
| Velocity Head (concrete lining) |  |  | m | 0.11676 | 0.023888 | 0.096501 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.033285 | 0.01962 | 0.012586 | 0.011506 | 0.011801
2.1.1 | Bend Loss in Tunnel
| Bend radius |  | R | m | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Rb/D |  | Rb/D |  | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.08 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
| Bend angle |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
| Bend Coefficient |  |  |  | 0.032 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
| Total bend loss in tunnel |  |  | m | 0.0024976 | 0.00063874 | 0.0025803 | 0.003122 | 0.003122 | 0.003122 | 0.003122 | 0.003122 | 0.00088999 | 0.0005246 | 0.00033653 | 0.00030766 | 0.00031555 | #REF! | #REF!
| Bend radius |  | R | m | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Rb/D |  | Rb/D |  | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625 | 15.625
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.08 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65
| Bend angle |  |  |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
| Bend Coefficient |  |  |  | 0.052 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
| Total bend loss in tunnel |  |  | m | 0.0040586 | 0.001038 | 0.004193 | 0.0050732 | 0.0050732 | 0.0050732 | 0.0050732 | 0.0050732 | 0.0014462 | 0.00085248 | 0.00054686 | 0.00049995 | 0.00051277 | -0.0040586 | -22.0041
| Total Bend loss in HRT |  |  |  | 0.0065562 | 0.0016767 | 0.0067733 | 0.0081952 | 0.0081952 | 0.0081952 | 0.0081952 | 0.0081952 | 0.0023362 | 0.0013771 | 0.0008834 | 0.00080761 | 0.00082832 | bar: Bend Loss Coefficient (K) 20
| TOTAL HEADLOSS IN HRT |  |  |  | 7.9602 | 1.6289 | 6.5805 | 7.9619 | 7.9619 | 7.9619 | 7.9619 | 7.9619 | 2.2697 | 1.3379 | 0.85824 | 0.78461 | 0.80473 | bar: Bend Loss Coefficient (K) 20
| total energy level |  |  | masl | 2470.5295 | 2479.6529 | 2472.5183 | 2470.5278 | 2470.5278 | 2470.5278 | 2470.5278 | 2470.5278 | 2478.7296 | 2480.0723 | 2480.7634 | 2480.8695 | 2480.8405
| Total water level |  |  | masl | 2470.4514 | 2479.6369 | 2472.4538 | 2470.4498 | 2470.4498 | 2470.4498 | 2470.4498 | 2470.4498 | 2478.7074 | 2480.0592 | 2480.755 | 2480.8618 | 2480.8326
2.2 | Contraction loss due to transition of penstock
| Coefficient of contraction |  | kc |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Dia of Penstock |  | d | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Velocity in Penstock |  | v | m/s | 3.9809 | 1.8006 | 3.6191 | 3.9809 | 3.9809 | 3.9809 | 3.9809 | 3.9809 | 2.1255 | 1.6318 | 1.307 | 1.2497 | 1.2656
| Loss due to contraction | Hcontraction=kc*V2/2g | Hc | m | 0.24232 | 0.049576 | 0.20027 | 0.24232 | 0.24232 | 0.24232 | 0.24232 | 0.24232 | 0.069077 | 0.040718 | 0.02612 | 0.023879 | 0.024492 | #REF! | #REF!
| Loss due to contraction |  |  | m | 0.24232 | 0.049576 | 0.20027 | 0.24232 | 0.24232 | 0.24232 | 0.24232 | 0.24232 | 0.069077 | 0.040718 | 0.02612 | 0.023879 | 0.024492
| Velocity head in shotcrete lined tunnel |  | Vt²/2g | m | 0.11676 | 0.023888 | 0.096501 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.11676 | 0.033285 | 0.01962 | 0.012586 | 0.011506 | 0.011801
| Tunnel head loss coeficient |  |  |  | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754 | 2.0754
2.3 | PENSTOCK INLET VALVE
| Discharge |  | Q | m3/s | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974
| Diameter of Valve |  | Dv | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Cross Sectional Area |  | Av | m2 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416
| Velocity |  | Vv | m/s | 3.9789 | 1.7997 | 3.6173 | 3.9789 | 3.9789 | 3.9789 | 3.9789 | 3.9789 | 2.1244 | 1.631 | 1.3063 | 1.249 | 1.265
| Velocity head |  | V2/(2*g) |  | 0.8069 | 0.16509 | 0.6669 | 0.8069 | 0.8069 | 0.8069 | 0.8069 | 0.8069 | 0.23002 | 0.13559 | 0.086979 | 0.079517 | 0.081556
| Loss Coefficient for valve |  | Kv |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Valve loss |  |  | m | 0.40345 | 0.082543 | 0.33345 | 0.40345 | 0.40345 | 0.40345 | 0.40345 | 0.40345 | 0.11501 | 0.067794 | 0.04349 | 0.039758 | 0.040778 | #REF! | #REF!
| TOTAL HEADLOSS IN TUNNEL AFTER SURGE SHAFT |  |  | m | 0.64577 | 0.13212 | 0.53373 | 0.64577 | 0.64577 | 0.64577 | 0.64577 | 0.64577 | 0.18409 | 0.10851 | 0.06961 | 0.063638 | 0.06527
| total energy level |  |  | masl | 2469.8837 | 2479.5207 | 2471.9845 | 2469.8821 | 2469.8821 | 2469.8821 | 2469.8821 | 2469.8821 | 2478.5455 | 2479.9638 | 2480.6938 | 2480.8058 | 2480.7752
| Total water level |  |  | masl | 2469.0768 | 2479.3557 | 2471.3176 | 2469.0752 | 2469.0752 | 2469.0752 | 2469.0752 | 2469.0752 | 2478.3155 | 2479.8282 | 2480.6068 | 2480.7263 | 2480.6936
2.4 | PENSTOCK PIPE of 2m dia
2.4.1 | PENSTOCK PIPE FRICTIONAL LOSS
| Design Discharge |  | Q | m3/s | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974
| Discharge to plant |  |  |  | 12.5 | 5.654 | 11.364 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 6.674 | 5.124 | 4.104 | 3.924 | 3.974
| Manning's Roughness Coefficient for Penstock Pipe |  | f |  | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
| Pipe length |  | Lp | m | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175 | 1201.175
| Pipe diameter |  | Dp | m | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Pipe area |  | AP | m2 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416 | 3.1416
| Flow velocity in pipe |  | Vp | m/s | 3.9789 | 1.7997 | 3.6173 | 3.9789 | 3.9789 | 3.9789 | 3.9789 | 3.9789 | 2.1244 | 1.631 | 1.3063 | 1.249 | 1.265
| Velocity Head |  |  |  | 0.8069 | 0.16509 | 0.6669 | 0.8069 | 0.8069 | 0.8069 | 0.8069 | 0.8069 | 0.23002 | 0.13559 | 0.086979 | 0.079517 | 0.081556
| Headloss due to friction | (Hf = fLV2/2gD ) | Hf | m | 6.3 | 1.2889 | 5.2069 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 1.7959 | 1.0586 | 0.6791 | 0.62084 | 0.63676 | #REF! | #REF!
| Rb/D |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| B (bend loss coefficient) |  |  |  | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
2.4.2 | PENSTOCK BEND LOSS
| Calculated for six 90 degree bends |  |  | m | 0.43573 | 0.089147 | 0.36013 | 0.43573 | 0.43573 | 0.43573 | 0.43573 | 0.43573 | 0.12421 | 0.073217 | 0.046969 | 0.042939 | 0.04404 | #REF! | #REF!
contraction loss from 2.0m to 1.2m
| Discharge after contraction |  |  |  | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| Dia after contraction |  |  | m | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| Velocity after contraction |  | Vc | m/s | 3.6841 | 2.4996 | 3.3493 | 3.6841 | 3.6841 | 3.6841 | 3.6841 | 3.6841 | 2.9506 | 2.2653 | 3.6287 | 3.4696 | 3.5138
Coefficient of loss for cylindrical contraction (Guideline for design of Intake for Hydroelectric Plant, ASCE, page no 58)
|  | 0.23333 | Ct |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Velocity head |  |  |  | 0.69179 | 0.31845 | 0.57176 | 0.69179 | 0.69179 | 0.69179 | 0.69179 | 0.69179 | 0.44372 | 0.26155 | 0.67114 | 0.61356 | 0.62929
| Contraction loss | Hcontraction=kc*V2/2g |  | m | 0.34589 | 0.15923 | 0.28588 | 0.34589 | 0.34589 | 0.34589 | 0.34589 | 0.34589 | 0.22186 | 0.13077 | 0.33557 | 0.30678 | 0.31465
Friction loss after trifurcation
| Design Discharge |  | Q | m3/s | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| Discharge to plant |  |  |  | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| Manning's Roughness Coefficient for Penstock Pipe |  | f |  | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
| Pipe length |  | Lp | m | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
| Pipe diameter |  | Dp | m | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| Pipe area |  | AP | m2 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131 | 1.131
| Flow velocity in pipe |  | Vp | m/s | 3.6841 | 2.4996 | 3.3493 | 3.6841 | 3.6841 | 3.6841 | 3.6841 | 3.6841 | 2.9506 | 2.2653 | 3.6287 | 3.4696 | 3.5138
| Velocity Head |  |  |  | 0.69179 | 0.31845 | 0.57176 | 0.69179 | 0.69179 | 0.69179 | 0.69179 | 0.69179 | 0.44372 | 0.26155 | 0.67114 | 0.61356 | 0.62929
| Headloss due to friction | (Hf = fLV2/2gD ) | Hf | m | 0.20984 | 0.096598 | 0.17343 | 0.20984 | 0.20984 | 0.20984 | 0.20984 | 0.20984 | 0.13459 | 0.079337 | 0.20358 | 0.18611 | 0.19089 | #REF! | #REF!
Friction loss for 0.9m pipe
| Design Discharge |  | Q | m3/s | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| Discharge to plant |  |  |  | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| Manning's Roughness Coefficient for Penstock Pipe |  | f |  | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
| Pipe length |  | Lp | m | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Pipe diameter |  | Dp | m | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Pipe area |  | AP | m2 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617 | 0.63617
| Flow velocity in pipe |  | Vp | m/s | 6.5496 | 4.4438 | 5.9544 | 6.5496 | 6.5496 | 6.5496 | 6.5496 | 6.5496 | 5.2454 | 4.0272 | 6.4511 | 6.1681 | 6.2467
| Velocity Head |  |  |  | 2.1864 | 1.0065 | 1.8071 | 2.1864 | 2.1864 | 2.1864 | 2.1864 | 2.1864 | 1.4024 | 0.82663 | 2.1211 | 1.9391 | 1.9889
| Headloss due to friction | (Hf = fLV2/2gD ) | Hf | m | 0.25265 | 0.1163 | 0.20882 | 0.25265 | 0.25265 | 0.25265 | 0.25265 | 0.25265 | 0.16205 | 0.095521 | 0.24511 | 0.22408 | 0.22983 | -0.25265 | -2.439
contraction loss from 2.0m to 1.2m
| Discharge after contraction |  |  |  | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| Dia after contraction |  |  | m | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| Velocity after contraction |  | Vc | m/s | 3.6841 | 2.4996 | 3.3493 | 3.6841 | 3.6841 | 3.6841 | 3.6841 | 3.6841 | 2.9506 | 2.2653 | 3.6287 | 3.4696 | 3.5138
Coefficient of loss for cylindrical contraction (Guideline for design of Intake for Hydroelectric Plant, ASCE, page no 58)
|  | 0.23333 | Ct |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Velocity head |  |  |  | 0.88487 | 0.40734 | 0.73134 | 0.88487 | 0.88487 | 0.88487 | 0.88487 | 0.88487 | 0.56756 | 0.33455 | 0.85845 | 0.7848 | 0.80493
| Contraction loss | Hcontraction=kc*V2/2g |  | m | 0.44243 | 0.20367 | 0.36567 | 0.44243 | 0.44243 | 0.44243 | 0.44243 | 0.44243 | 0.28378 | 0.16727 | 0.42923 | 0.3924 | 0.40246
1.0728
| Bend radius |  | R | m | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| Rb/D |  | Rb/D |  | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667
| B | from NTNU vol 8 Fig 7.1 |  |  | 0.09 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Correction | From NTNU vol 8 fig 7.2 |  |  | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| bend loss |  | Ѳ |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
| Loss coefficient for 45 degreebend |  | B |  | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063 | 0.063
| Head Loss due to bifurcation bend |  | HL | m | 0.13774 | 0.063408 | 0.11384 | 0.13774 | 0.13774 | 0.13774 | 0.13774 | 0.13774 | 0.08835 | 0.052077 | 0.13363 | 0.12217 | 0.1253
Spherical valve loss
| Discharge | 12.5 |  |  | 4.1667 | 2.827 | 3.788 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 4.1667 | 3.337 | 2.562 | 4.104 | 3.924 | 3.974
| velocity | 19.6488 |  |  | 6.5496 | 4.4438 | 5.9544 | 6.5496 | 6.5496 | 6.5496 | 6.5496 | 6.5496 | 5.2454 | 4.0272 | 6.4511 | 6.1681 | 6.2467
| Valve loss coefficient | 0.1 |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| Valve diameter | 0.9 | [15 empty] | #REF! | #REF!
| C/S Area | 0.63617
| Head loss |  |  |  | 0.21864 | 0.10065 | 0.18071 | 0.21864 | 0.21864 | 0.21864 | 0.21864 | 0.21864 | 0.14024 | 0.082663 | 0.21211 | 0.19391 | 0.19889
|  |  | 4.9122 |  | 1.8 | 4.1667 | 1.6374 | 3.2748 |  | 0.78595 |  | 0.84823 | 0.92099 | 4.1667 | 0.84823 | #DIV/0! |  | #REF! | #REF!
| TOTAL HEADLOSS IN PENSTOCK |  |  | m | 8.3429 | 2.1179 | 6.8954 | 8.3429 | 8.3429 | 8.3429 | 8.3429 | 8.3429 | 2.951 | 1.7395 | 2.2853 | 2.0892 | 2.1428
| total energy level |  |  | masl | 2461.5408 | 2477.4028 | 2465.0891 | 2461.5391 | 2461.5391 | 2461.5391 | 2461.5391 | 2461.5391 | 2475.5945 | 2478.2243 | 2478.4085 | 2478.7166 | 2478.6324
| Total water level |  |  | masl | 2460.849 | 2477.0844 | 2464.5173 | 2460.8473 | 2460.8473 | 2460.8473 | 2460.8473 | 2460.8473 | 2475.1508 | 2477.9627 | 2477.7373 | 2478.103 | 2478.0031
| Penstock head loss coeficient |  |  |  | 10.3395 | 12.8292 | 10.3395 | 10.3395 | 10.3395 | 10.3395 | 10.3395 | 10.3395 | 12.8292 | 12.8292 | 26.274 | 26.274 | 26.274
4 | OTHER MINOR LOSSES
| Other minor losses such as tappering and epansion in bifurcated pipe etc |  |  | m | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Other minor loss coefficient
| TOTAL HEAD LOSS |  |  | m | 20.996 | 5.1047 | 17.4413 | 20.9977 | 20.9977 | 20.9977 | 20.9977 | 20.9977 | 6.916 | 4.2819 | 4.0955 | 3.787 | 3.8713
[6 empty] | 5.1047 | 17.4413 | 20.9977 | 20.9977 | 20.9977 | 20.9977 | 20.9977 | 6.916 | 4.2819 | 4.0955 | 3.787 | 3.8713
|  | Head Loss Calculated | Gross Head | Net Head
| Month | 5.1047 | 629 | 623.8953
| Baisakh | 17.4413 | 629 | 611.5587
| Jestha | 20.9977 | 629 | 608.0023
| Asar | 20.9977 | 629 | 608.0023
| Shrawan | 20.9977 | 629 | 608.0023 | [18 empty] | Bend Loss Coefficient (K) 10: Head Loss; Bend Loss Coefficient (K) 20: Gross Head; Bend Loss Coefficient (K) 30: Net Head
| Bhadra | 20.9977 | 629 | 608.0023 | [17 empty] | Baisakh | Bend Loss Coefficient (K) 10: 5.1047; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 622.8708
| Ashoj | 20.9977 | 629 | 608.0023 | [17 empty] | Jestha | Bend Loss Coefficient (K) 10: 17.4413; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 605.7596
| Kartik | 6.916 | 629 | 622.084 | [17 empty] | Asar | Bend Loss Coefficient (K) 10: 20.9977; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 600.9858
| Mangsir | 4.2819 | 629 | 624.7181 | [17 empty] | Shrawan | Bend Loss Coefficient (K) 10: 20.9977; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 600.9858
| Poush | 4.0955 | 629 | 624.9045 | [17 empty] | Bhadra | Bend Loss Coefficient (K) 10: 20.9977; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 600.9858
| Magh | 3.787 | 629 | 625.213 | [17 empty] | Ashoj | Bend Loss Coefficient (K) 10: 20.9977; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 600.9858
| Falgun | 3.8713 | 629 | 625.1287 | [17 empty] | Kartik | Bend Loss Coefficient (K) 10: 20.9977; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 600.9858
| Chaitra | [20 empty] | Mangsir | Bend Loss Coefficient (K) 10: 6.916; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 620.6565
[22 empty] | Poush | Bend Loss Coefficient (K) 10: 4.2819; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 623.8767
[22 empty] | Magh | Bend Loss Coefficient (K) 10: 4.0955; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 625.5341
[22 empty] | Falgun | Bend Loss Coefficient (K) 10: 3.787; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 625.7886
[22 empty] | Chaitra | Bend Loss Coefficient (K) 10: 3.8713; Bend Loss Coefficient (K) 20: 629; Bend Loss Coefficient (K) 30: 625.7191
D
D/2
D/2
Note on C52: Author: V=Cd.sqrt(2.g.head diff.) or, head loss = (1/Cd²).V²/(2.g)
Note on F81: Author: Bottom width adopted
Note on F82: Author: adopt depth of storage
Note on F139: Author: frm drawing
Note on G139: Author: from drawing
Note on F215: Bishal Koirala: Avg depth
Note on C243: Author: V=Cd.sqrt(2.g.head diff.) or, head loss = (1/Cd²).V²/(2.g)
Note on F294: Author: This coefficient as the multiple of square of approach canal velovity is used for the estimation of head loss at headworks under various discharge
Note on F302: Pravash Mool: 0.0041 from moody's diagram
Note on D429: Author: 0.5-2 for butterfly valve
Note on F440: Author: GDIHP, Pg 57, Table for Manning's Roughness Coefficient
Note on F458: Author: 0.42*(1-(db/dp)^2)
Note on F466: Author: GDIHP, Pg 57, Table for Manning's Roughness Coefficient
Note on F477: Author: GDIHP, Pg 57, Table for Manning's Roughness Coefficient
Note on F490: Author: 0.42*(1-(db/dp)^2)
Note on C505: Author: From fig 4 11625 1986 for diamter 2.2m and 1.506 Mpa

## Sheet1
Pipe
k | 1 | mm
D | 1200 | mm
k/D | 0.00083333
Q | 12.5 | m3/s
D | 1.2 | m
A | 1.131 | m2
U | 11.0524 | m/s
v | 1e-06 | m2/s
Re | 13262911.9243
f | 0.0045 | estimated

## HL calculation_Coefficient (hidden)
Headloss Calculation
Total head loss | 22 | m
Design Q | 12.51
Coefficient | 0.14057
Month | Power generating flow | System head loss |  | Adopted HL
| m3/s | m
Baisakh | 5.654 | 4.5 | 4.8605 | 4.8605
Jestha | 11.364 | 18.2 | 19.8357 | 19.8357
Asar | 12.5 | 22 | 21.8206 | 22
Shrawan | 12.5 | 22 | 21.8206 | 22
Bhadra | 12.5 | 22 | 21.8206 | 22
Ashoj | 12.5 | 22 | 21.8206 | 22
Kartik | 12.5 | 22 | 17.6894 | 22
Mangsir | 6.674 | 6.3 | 5.9211 | 6.3
Poush | 5.124 | 3.7 | 2.7414 | 3.7
Magh | 4.104 | 2.4 | 2.1553 | 2.4
Falgun | 3.924 | 2.2 | 2.1363 | 2.2
Chaitra | 3.974 | 2.3 | 2.3862 | 2.3862

## Energy
Myagdi Khola HPP
Power and Energy Calculation with PPA monthly flow
Assumptions and input parameters
Normal water level (Crest level at weir) |  |  |  | 2482 | masl
Turbine CL Level |  |  |  | 1853 | masl
Gross head |  |  |  | 629 | m
Turbine rated efficiency |  |  |  | 91.5%
Turbine efficiency for energy generation |  |  |  | 90.5%
Generator efficiency |  |  |  | 97%
Transformer efficiency |  |  |  | 99%
Overall efficiency |  |  |  | 87.87%
Rated net head, m |  |  |  | 608.0023 | m
Number of Units |  |  |  | 3
Design flow, m3/s |  |  |  | 12.5 | m3/s
Design flow, m3/s (Generation License) |  |  |  | 12.5 | m3/s
Per Unit Design flow, m3/s |  |  |  | 4.1667 | m3/s
Downsrtream release |  |  |  | 0.436 | m3/s
Dry season outage + Self consumption |  |  |  | 4%
Wet season outage + Self consumption |  |  |  | 4%
Installed Capacity (PPA) |  |  |  | 57.3 | MW
Installed Capacity |  |  |  | 65000 | KW
Month | Mean monthly Flow | D/S release | Available flow | Diverted flow for power generation | Total Head loss | Net Head | Efficiency |  | Average monthly power | Operating days | Monthly energy generation | Outage & self consumption | Generated Net energy for revenue |  | Saleable Net energy for revenue |  | Generated Net Energy |  | PPA Energy |  | Saleable Net energy for revenue |  | % difference between PPA energy and Saleable energy | [5 empty] | PPA Energy
[7 empty] | Turbine efficiency | Overall efficiency |  |  |  |  | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy |  | Mean Monthly Flow |  |  | Dry season energy | Wet season energy
| (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m) | (m) | % | % | (kW) |  | (KWh) | (KWh) | (KWh) | (KWh) | (KWh) | (KWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | Month | UFSR flow | HCE flow | PPA flow | (GWh) | (GWh)
Baisakh | 6.09 | 0.436 | 5.654 | 5.654 | 5.1047 | 623.8953 | 91.5% | 87.87% | 30713.5022 | 31 | 22622337.1441 | 904893.4858 | 21717443.6583 |  | 19084875 |  | 21.7174 |  | 19.0849 |  | 19.0849 |  | 0% |  | Baisakh | 6 | 6.09 | 6.09 | 19.0849
Jestha | 11.8 | 0.436 | 11.364 | 11.364 | 17.4413 | 611.5587 | 91.5% | 87.87% | 60510.5634 | 31 | 44569660.5895 | 1782786.4236 | [12 empty] | Jestha | 10.79 | 12.3444 | 11.8
Jestha 1-15 | [9 empty] | 15 |  |  | 20703326.2093 |  | 18197752 |  | 20.7033 |  | 18.1978 |  | 18.1978 |  | 0% |  | Jestha 1-15 |  |  |  | 18.1978
Jestha 16 onwards | [9 empty] | 16 |  |  |  | 22083547.9566 |  | 19410935 |  | 22.0835 |  | 19.4109 |  | 19.4109 |  | 0% | Jestha 16 onwards |  |  |  |  | 19.4109
Asar | 45.42 | 0.436 | 44.984 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 32 | 49420800 | 1976832 |  | 47443968 |  | 41823683 |  | 47.444 |  | 41.8237 |  | 41.8237 |  | 0% | Asar | 42.62 | 45.42 | 45.42 |  | 41.8237
Shrawan | 73.28 | 0.436 | 72.844 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 31 | 47876400 | 1915056 |  | 45961344 |  | 40516692 |  | 45.9613 |  | 40.5167 |  | 40.5167 |  | 0% | Shrawan | 81.43 | 55.6624 | 73.28 |  | 40.5167
Bhadra | 65.41 | 0.436 | 64.974 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 31 | 47876400 | 1915056 |  | 45961344 |  | 40516692 |  | 45.9613 |  | 40.5167 |  | 40.5167 |  | 0% | Bhadra | 68.07 | 47.6435 | 65.41 |  | 40.5167
Ashoj | 36.1 | 0.436 | 35.664 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 31 | 47876400 | 1915056 |  | 45961344 |  | 40516692 |  | 45.9613 |  | 40.5167 |  | 40.5167 |  | 0% | Ashoj | 33.14 | 27.157 | 36.1 |  | 40.5167
Kartik | 13.49 | 0.436 | 13.054 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 30 | 46332000 | 1853280 |  | 44478720 |  | 39209702 |  | 44.4787 |  | 39.2097 |  | 39.2097 |  | 0% | Kartik | 13.78 | 11.6596 | 13.49 |  | 39.2097
Mangsir | 7.11 | 0.436 | 6.674 | 6.674 | 6.916 | 622.084 | 91.5% | 87.87% | 36149.0654 | 29 | 24908152.0201 | 996326.0808 | [9 empty] | 0 |  |  | Mangsir | 7.86 | 6.7443 | 7.11
Mangsir 1-15 | [9 empty] | 15 |  |  |  | 12368185.8307 |  | 10889794 |  | 12.3682 |  | 10.8898 |  | 10.8898 |  | 0% | Mangsir 1-15 |  |  |  |  | 10.8898
Mangsir 16 onwards | [9 empty] | 14 |  |  | 11543640.1086 |  | 10163809 |  | 11.5436 |  | 10.1638 |  | 10.1638 |  | 0% |  | Mangsir 16 onwards |  |  |  | 10.1638
Poush | 5.56 | 0.436 | 5.124 | 5.124 | 4.2819 | 624.7181 | 91.5% | 87.87% | 27871.1602 | 30 | 19866562.9722 | 794662.5189 | 19071900.4533 |  | 16756441 |  | 19.0719 |  | 16.7564 |  | 16.7564 |  | 0% |  | Poush | 5.72 | 4.4936 | 5.56 | 16.7564
Magh | 4.54 | 0.436 | 4.104 | 4.104 | 4.0955 | 624.9045 | 91.5% | 87.87% | 22329.6974 | 29 | 15386054.6844 | 615442.1874 | 14770612.497 |  | 12995863 |  | 14.7706 |  | 12.9959 |  | 12.9959 |  | 0% |  | Magh | 4.66 | 3.9166 | 4.54 | 12.9959
Falgun | 4.36 | 0.436 | 3.924 | 3.924 | 3.787 | 625.213 | 91.5% | 87.87% | 21360.8641 | 30 | 15226023.9206 | 609040.9568 | 14616982.9638 |  | 12890288 |  | 14.617 |  | 12.8903 |  | 12.8903 |  | 0% |  | Falgun | 4.17 | 3.896 | 4.36 | 12.8903
Chaitra | 4.41 | 0.436 | 3.974 | 3.974 | 3.8713 | 625.1287 | 91.5% | 87.87% | 21413.8282 | 30 | 15263776.7079 | 610551.0683 | 14653225.6396 |  | 13020546 |  | 14.6532 |  | 13.0205 |  | 13.0205 |  | 0% |  | Chaitra | 4.45 | 4.41 | 4.41 | 13.0205
Total | [9 empty] | 365 |  |  | 117077131.53 | 264258453.7873 | 103109574 | 232884190 | 117.0771 | 264.2585 | 103.1096 | 232.8842 | 103.1096 | 232.8842 | [6 empty] | 103.1096 | 232.8842
Annual energy generation, GWH | [12 empty] | 117.0771 | 264.2585 | 103.1096 | 232.8842 | 0.00011708 | 0.00026426 |  |  | 0.00010311 | 0.00023288 |  |  | Payable Energy |  |  |  | 0
|  |  |  | Energy Generated |  | PPA Energy |  |  | Diff | [19 empty] | 335.9938
Dry Season Energy, GWh |  |  |  | 117.0771 | 30.7% | 103.11 |  |  | 13.9671 | 30.8%
Wet season Energy, GWh |  |  |  | 264.2585 | 69.3% | 232.88 |  |  | 31.3785 | 69.2%
Total Annual Energy, GWh |  |  |  | 381.3356 | 100% | 335.99 |  |  | 45.3456 | 100%