## efficiency from chart (hidden)
% of Q | Efficiency from available energy curve
100 | 90.5%
90 | 90.5%
80 | 90.5%
70 | 90.5%
60 | 90.5%
50 | 90.5%
Overrating | 90.5%
Design discharge |  | 12.5 | m3/s
No of unit |  | 3
| Per unit discharge | 4.1667
Month | Power Generating Discharge, m³/s | Unit 1 | Unit 2 | Unit 3 | Efficiency | Remarks
Baishakh | 5.654 | 135.7% | 67.85% | 45.23% | 91% | 2 | 90%
Jestha | 11.364 | 272.7% | 136.4% | 90.91% | 91% | 3 | 91%
Ashadh | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Shrawan | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Bhadra | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Ashwin | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Kartik | 12.5 | 300% | 150% | 100% | 91% | 3 | 91%
Mangshir | 6.674 | 160.2% | 80.09% | 53.39% | 91% | 3 | 89%
Paush | 5.124 | 123% | 61.49% | 40.99% | 91% | 2 | 89%
Magh | 4.104 | 98.5% | 49.25% | 32.83% | 91% | 2 | 90%
Fagun | 3.924 | 94.18% | 47.09% | 31.39% | 91% | 1 | 89%
Chaitra | 3.974 | 95.38% | 47.69% | 31.79% | 91% | 1 | 90%
Note on G16: Jeevika Khadka: efficiency at rated discharge is 91

## Headloss Summary
Myagdi Khola HPP
Power and Energy Calculation with PPA monthly flow
SN | Component | Unit | Headloss | Baisakh | Jestha | Ashad | Srawan | Bhadra | Asoj | Kartik | Mangsir | Poush | Magh | Falgun | Chaitra
1 | TOTAL HEADLOSS IN HEADWORKS | m | 2.0402 | 0.41742 | 1.6863 | 2.0402 | 2.0402 | 2.0402 | 2.0402 | 2.0402 | 0.58161 | 0.34283 | 0.21993 | 0.20106 | 0.20621
2 | TOTAL HEADLOSS IN HEADRACE PIPE | m | 1.5069 | 0.3083 | 1.2454 | 1.5069 | 1.5069 | 1.5069 | 1.5069 | 1.5069 | 0.42957 | 0.25321 | 0.16243 | 0.1485 | 0.1523
3 | TOTAL HEADLOSS IN HRT | m | 7.9602 | 1.6289 | 6.5805 | 7.9619 | 7.9619 | 7.9619 | 7.9619 | 7.9619 | 2.2697 | 1.3379 | 0.85824 | 0.78461 | 0.80473
4 | TOTAL HEADLOSS AFTER SURGE SHAFT | m | 0.64577 | 0.13212 | 0.53373 | 0.64577 | 0.64577 | 0.64577 | 0.64577 | 0.64577 | 0.18409 | 0.10851 | 0.06961 | 0.063638 | 0.06527
5 | TOTAL HEADLOSS IN PENSTOCK | m | 8.3429 | 2.1179 | 6.8954 | 8.3429 | 8.3429 | 8.3429 | 8.3429 | 8.3429 | 2.951 | 1.7395 | 2.2853 | 2.0892 | 2.1428
6 | OTHER MINOR LOSSES | m | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| TOTAL | m | 20.996 | 5.1047 | 17.4413 | 20.9977 | 20.9977 | 20.9977 | 20.9977 | 20.9977 | 6.916 | 4.2819 | 4.0955 | 3.787 | 3.8713

## HL calculation_Coefficient (hidden)
Headloss Calculation
Total head loss | 22 | m
Design Q | 12.51
Coefficient | 0.14057
Month | Power generating flow | System head loss |  | Adopted HL
| m3/s | m
Baisakh | 5.654 | 4.5 | 4.8605 | 4.8605
Jestha | 11.364 | 18.2 | 19.8357 | 19.8357
Asar | 12.5 | 22 | 21.8206 | 22
Shrawan | 12.5 | 22 | 21.8206 | 22
Bhadra | 12.5 | 22 | 21.8206 | 22
Ashoj | 12.5 | 22 | 21.8206 | 22
Kartik | 12.5 | 22 | 17.6894 | 22
Mangsir | 6.674 | 6.3 | 5.9211 | 6.3
Poush | 5.124 | 3.7 | 2.7414 | 3.7
Magh | 4.104 | 2.4 | 2.1553 | 2.4
Falgun | 3.924 | 2.2 | 2.1363 | 2.2
Chaitra | 3.974 | 2.3 | 2.3862 | 2.3862

## Energy
Myagdi Khola HPP
Power and Energy Calculation with PPA monthly flow
Assumptions and input parameters
Normal water level (Crest level at weir) |  |  |  | 2482 | masl
Turbine CL Level |  |  |  | 1853 | masl
Gross head |  |  |  | 629 | m
Turbine rated efficiency |  |  |  | 91.5%
Turbine efficiency for energy generation |  |  |  | 90.5%
Generator efficiency |  |  |  | 97%
Transformer efficiency |  |  |  | 99%
Overall efficiency |  |  |  | 87.87%
Rated net head, m |  |  |  | 600.7093 | m
Number of Units |  |  |  | 3
Design flow, m3/s |  |  |  | 12.5 | m3/s
Design flow, m3/s (Generation License) |  |  |  | 12.5 | m3/s
Per Unit Design flow, m3/s |  |  |  | 4.1667 | m3/s
Downsrtream release |  |  |  | 0.436 | m3/s
Dry season outage + Self consumption |  |  |  | 4%
Wet season outage + Self consumption |  |  |  | 4%
Installed Capacity (PPA) |  |  |  | 57.3 | MW
Installed Capacity |  |  |  | 65000 | KW
Month | Mean monthly Flow | D/S release | Available flow | Diverted flow for power generation | Total Head loss | Net Head | Efficiency |  | Average monthly power | Operating days | Monthly energy generation | Outage & self consumption | Generated Net energy for revenue |  | Saleable Net energy for revenue |  | Generated Net Energy |  | PPA Energy |  | Saleable Net energy for revenue |  | % difference between PPA energy and Saleable energy |  |  |  |  | PPA Energy
[7 empty] | Turbine efficiency | Overall efficiency |  |  |  |  | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy | Dry season energy | Wet season energy |  | Mean Monthly Flow |  | Dry season energy | Wet season energy
| (m3/s) | (m3/s) | (m3/s) | (m3/s) | (m) | (m) | % | % | (kW) |  | (KWh) | (KWh) | (KWh) | (KWh) | (KWh) | (KWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | (GWh) | Month |  | PPA flow | (GWh) | (GWh)
Baisakh | 6.09 | 0.436 | 5.654 | 5.654 | 5.1047 | 623.8953 | 91.5% | 87.87% | 30713.5022 | 31 | 22622337.1441 | 904893.4858 | 21717443.6583 |  | 19084875 |  | 21.5323 |  | 19.0849 |  | 19.0849 |  | 0% |  | Baisakh |  | 6.09 | 19.0849
Jestha | 11.8 | 0.436 | 11.364 | 11.364 | 17.4413 | 611.5587 | 91.5% | 87.87% | 60510.5634 | 31 | 44569660.5895 | 1782786.4236 | [12 empty] | Jestha |  | 11.8
Jestha 1-15 | [9 empty] | 15 |  |  | 20703326.2093 |  | 18197752 |  | 20.1749 |  | 18.1978 |  | 18.1978 |  | 0% |  | Jestha 1-15 |  |  | 18.1978
Jestha 16 onwards | [9 empty] | 16 |  |  |  | 22083547.9566 |  | 19410935 |  | 21.5199 |  | 19.4109 |  | 19.4109 |  | 0% | Jestha 16 onwards |  |  |  | 19.4109
Asar | 45.42 | 0.436 | 44.984 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 32 | 49420800 | 1976832 |  | 47443968 |  | 41823683 |  | 46.9498 |  | 41.8237 |  | 41.8237 |  | 0% | Asar |  | 45.42 |  | 41.8237
Shrawan | 73.28 | 0.436 | 72.844 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 31 | 47876400 | 1915056 |  | 45961344 |  | 40516692 |  | 45.4826 |  | 40.5167 |  | 40.5167 |  | 0% | Shrawan |  | 73.28 |  | 40.5167
Bhadra | 65.41 | 0.436 | 64.974 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 31 | 47876400 | 1915056 |  | 45961344 |  | 40516692 |  | 45.4826 |  | 40.5167 |  | 40.5167 |  | 0% | Bhadra |  | 65.41 |  | 40.5167
Ashoj | 36.1 | 0.436 | 35.664 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 31 | 47876400 | 1915056 |  | 45961344 |  | 40516692 |  | 45.4826 |  | 40.5167 |  | 40.5167 |  | 0% | Ashoj |  | 36.1 |  | 40.5167
Kartik | 13.49 | 0.436 | 13.054 | 12.5 | 20.9977 | 608.0023 | 91.5% | 87.87% | 65000 | 30 | 46332000 | 1853280 |  | 44478720 |  | 39209702 |  | 44.0154 |  | 39.2097 |  | 39.2097 |  | 0% | Kartik |  | 13.49 |  | 39.2097
Mangsir | 7.11 | 0.436 | 6.674 | 6.674 | 6.916 | 622.084 | 91.5% | 87.87% | 36149.0654 | 29 | 24908152.0201 | 996326.0808 | [9 empty] | 0 |  |  | Mangsir |  | 7.11
Mangsir 1-15 | [9 empty] | 15 |  |  |  | 12368185.8307 |  | 10889794 |  | 12.1201 |  | 10.8898 |  | 10.8898 |  | 0% | Mangsir 1-15 |  |  |  | 10.8898
Mangsir 16 onwards | [9 empty] | 14 |  |  | 11543640.1086 |  | 10163809 |  | 11.3121 |  | 10.1638 |  | 10.1638 |  | 0% |  | Mangsir 16 onwards |  |  | 10.1638
Poush | 5.56 | 0.436 | 5.124 | 5.124 | 4.2819 | 624.7181 | 91.5% | 87.87% | 27871.1602 | 30 | 19866562.9722 | 794662.5189 | 19071900.4533 |  | 16756441 |  | 18.9198 |  | 16.7564 |  | 16.7564 |  | 0% |  | Poush |  | 5.56 | 16.7564
Magh | 4.54 | 0.436 | 4.104 | 4.104 | 4.0955 | 624.9045 | 91.5% | 87.87% | 22329.6974 | 29 | 15386054.6844 | 615442.1874 | 14770612.497 |  | 12995863 |  | 14.6376 |  | 12.9959 |  | 12.9959 |  | 0% |  | Magh |  | 4.54 | 12.9959
Falgun | 4.36 | 0.436 | 3.924 | 3.924 | 3.787 | 625.213 | 91.5% | 87.87% | 21360.8641 | 30 | 15226023.9206 | 609040.9568 | 14616982.9638 |  | 12890288 |  | 14.4898 |  | 12.8903 |  | 12.8903 |  | 0% |  | Falgun |  | 4.36 | 12.8903
Chaitra | 4.41 | 0.436 | 3.974 | 3.974 | 3.8713 | 625.1287 | 91.5% | 87.87% | 21413.8282 | 30 | 15263776.7079 | 610551.0683 | 14653225.6396 |  | 13020546 |  | 14.5245 |  | 13.0205 |  | 13.0205 |  | 0% |  | Chaitra |  | 4.41 | 13.0205
Total | [9 empty] | 365 |  |  | 117077131.53 | 264258453.7873 | 103109574 | 232884190 | 115.591 | 261.0529 | 103.1096 | 232.8842 | 103.1096 | 232.8842 | [5 empty] | 103.1096 | 232.8842
Annual energy generation, GWH | [12 empty] | 117.0771 | 264.2585 | 103.1096 | 232.8842 | 0.00011559 | 0.00026105 |  |  | 0.00010311 | 0.00023288 |  |  | Payable Energy |  |  | 0
|  |  |  | Energy Generated |  | PPA Energy |  |  | Diff | [18 empty] | 335.9938
Dry Season Energy, GWh |  |  |  | 117.0771 | 30.7% | 103.11 |  |  | 13.9671 | 30.8%
Wet season Energy, GWh |  |  |  | 264.2585 | 69.3% | 232.88 |  |  | 31.3785 | 69.2%
Total Annual Energy, GWh |  |  |  | 381.3356 | 100% | 335.99 |  |  | 45.3456 | 100%